## N1
supply_temp | return_temp | ct_conductivity | ct_ph | Bore | CWRO | BoilerBD | BD | scheme | mu_conductivity | mu_flow(PV) | mu_flow(OV) | m-saving(PV-OV) | mu_ph | cooling_tower_level | relative_humidity | ambient_temp | delta_temp | wetBulb_temp | approach_temp | cond_coc | ct_tds | ct_ca | ct_alk | ct_chloride | flow_cycle | sat_index | sta_index | perf_index | system_vol | rec_rate | evap_loss | drift_loss | blowdown_coc | hold_time_index | dosing_residual | dosing_contact_time | dosing_density | dosing_continuous | dosing_initial | dosing_slug | currentOperatingCost | newOperatingCost | updatedDateTime | 1651.3952 | 5.2083
19.81 | 30.37 | 5473.84 | 7.6 | [48.38, 48.38] | [25.03, 25.03] | [8.02, 8.02] | [5.34, 5.34] | 0 | 955.25 | 81.43 | 81.43 | 0 | 7.36 | 89.1 | 44 | 22.5 | 10.56 | 14.96 | 4.85 | 5.73 | 3503.26 | 1034.58 | 1162.87 | 724.74 | 15.25 | 1.54 | 4.52 | 68.53 | 490 | 4700 | 75.9 | 0.47 | 16.05 | 63.58 | 60 | 9 | 9 | 0.36 | 294 | 297.2 | 410666.14 | 410666.14 | 20230204-160652_2002ecfe-bd5b-4d66-b73c-bc6b1d75d014 | 0
19.67 | 30.4 | 5536.5 | 7.32 | [35.34, 54.82] | [24.91, 11.84] | [9.55, 9.55] | [4.47, 10.89] | 0 | 833.31 | 69.8 | 76.21 | -6.41 | 7.29 | 88.48 | 46 | 21.7 | 10.73 | 14.59 | 5.08 | 6.64 | 3543.36 | 1051.52 | 1227.1 | 746.39 | 6.41 | 1.28 | 4.75 | 67.89 | 490 | 4700 | 77.17 | 0.47 | 13.67 | 31.19 | 60 | 9 | 9 | 0.73 | 294 | 300.53 | 390225.17 | 312241.27 | 20230204-160652_99555fc7-8c3b-4882-a6f7-4504d0b92880 | 4.4511
19.66 | 30.39 | 5492.59 | 7.61 | [44.08, 48.64] | [25.0, 20.54] | [8.32, 8.32] | [9.59, 9.69] | 0 | 920.63 | 77.4 | 77.5 | -0.1 | 7.34 | 88.94 | 63 | 19.9 | 10.74 | 15.3 | 4.35 | 5.97 | 3515.26 | 1039.22 | 1178.32 | 730.14 | 7.99 | 1.55 | 4.51 | 71.16 | 490 | 4700 | 77.2 | 0.47 | 15.55 | 35.05 | 60 | 9 | 9 | 0.65 | 294 | 299.81 | 449913.53 | 400227.41 | 20230204-160652_112b7c4b-48f6-4fee-9835-c897f50db736 | 2.836
20.63 | 31.26 | 5468.06 | 7.6 | [29.5, 63.24] | [24.97, 1.76] | [10.16, 10.16] | [2.0, 12.53] | 0 | 763.59 | 64.63 | 75.16 | -10.53 | 7.25 | 89.35 | 87 | 17.2 | 10.64 | 15.66 | 4.97 | 7.16 | 3499.56 | 1041.9 | 1246.32 | 746.1 | 5.16 | 1.59 | 4.43 | 68.16 | 490 | 4700 | 76.48 | 0.47 | 12.41 | 27.11 | 60 | 9 | 9 | 0.84 | 294 | 301.52 | 361309.26 | 213143.1 | 20230204-160652_e00046a6-6eb4-4c3d-a232-5e88faccf455 | 8.457
19.42 | 30.12 | 5462.38 | 7.6 | [50.33, 50.33] | [25.0, 25.0] | [8.62, 8.62] | [8.79, 8.79] | 0 | 964.47 | 83.95 | 83.95 | 0 | 7.37 | 88.81 | 63 | 19.6 | 10.69 | 15.03 | 4.39 | 5.66 | 3495.92 | 1032.85 | 1162.67 | 724.13 | 9.55 | 1.53 | 4.55 | 70.88 | 490 | 4700 | 76.89 | 0.47 | 16.49 | 38.63 | 60 | 9 | 9 | 0.59 | 294 | 299.27 | 447520.42 | 447520.42 | 20230204-160652_fab0dbb8-028f-4138-acb0-0f679b3742bd | 0
18.76 | 29.49 | 5491.48 | 7.59 | [24.62, 47.63] | [24.87, 9.31] | [9.25, 9.25] | [2.01, 9.46] | 0 | 707.45 | 58.74 | 66.19 | -7.45 | 7.2 | 88.91 | 68 | 17.8 | 10.73 | 13.99 | 4.77 | 7.76 | 3514.55 | 1047.24 | 1267.35 | 752.33 | 6.21 | 1.55 | 4.49 | 69.24 | 490 | 4700 | 77.16 | 0.47 | 11.41 | 35.91 | 60 | 9 | 9 | 0.63 | 294 | 299.67 | 355088.04 | 260147.83 | 20230204-160652_6eb5ef77-735c-4259-917e-f1e351772977 | 5.419
19.72 | 30.51 | 5536.32 | 7.59 | [41.14, 50.97] | [24.94, 16.47] | [8.6, 8.6] | [8.78, 10.14] | 0 | 894.67 | 74.68 | 76.04 | -1.36 | 7.32 | 88.77 | 56 | 20.9 | 10.78 | 15.29 | 4.44 | 6.19 | 3543.24 | 1048.46 | 1197.62 | 738.52 | 7.37 | 1.55 | 4.5 | 70.85 | 490 | 4700 | 77.55 | 0.47 | 14.95 | 33.49 | 60 | 9 | 9 | 0.68 | 294 | 300.08 | 438596.58 | 357229.71 | 20230204-160652_d3ca2bbe-cc61-4fde-8bfc-9ffe281ed7a3 | 4.6442
20.12 | 30.76 | 5531.05 | 7.6 | [47.39, 47.39] | [25.01, 25.01] | [8.85, 8.85] | [6.51, 6.51] | 0 | 941.67 | 81.25 | 81.25 | 0 | 7.36 | 89.02 | 50 | 21.9 | 10.64 | 15.33 | 4.78 | 5.87 | 3539.87 | 1046.58 | 1184.98 | 735.21 | 12.48 | 1.56 | 4.49 | 68.99 | 490 | 4700 | 76.51 | 0.47 | 15.7 | 52.15 | 60 | 9 | 9 | 0.43 | 294 | 297.91 | 422128.9 | 422128.9 | 20230204-160652_270e0bcf-5337-4ce8-af48-c8601e639e04 | 0
19.39 | 30.01 | 5509.12 | 7.98 | [26.34, 59.73] | [25.03, 1.2] | [10.05, 10.05] | [2.28, 11.83] | 0 | 723.79 | 61.42 | 70.98 | -9.56 | 7.22 | 89.38 | 49 | 20.8 | 10.62 | 14.25 | 5.14 | 7.61 | 3525.84 | 1051.21 | 1272.99 | 755.86 | 5.19 | 1.96 | 4.07 | 67.38 | 490 | 4700 | 76.38 | 0.47 | 11.55 | 28.71 | 60 | 9 | 9 | 0.79 | 294 | 301.1 | 362003.54 | 196073.52 | 20230204-160652_39b8955b-2c79-4917-ac03-a0880fdbbd46 | 9.4709
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.04 | 29.62 | 5449.22 | 7.6 | [32.22, 45.58] | [25.01, 18.21] | [8.82, 8.82] | [2.52, 9.08] | 0 | 804.55 | 66.05 | 72.61 | -6.56 | 7.26 | 89.11 | 65 | 18.4 | 10.58 | 14.18 | 4.86 | 6.77 | 3487.5 | 1034.77 | 1210.3 | 734.63 | 7.28 | 1.54 | 4.52 | 68.52 | 490 | 4700 | 76.06 | 0.47 | 13.18 | 37.42 | 60 | 9 | 9 | 0.61 | 294 | 299.45 | 368249.43 | 363150.67 | 20230204-160652_d36adc95-942a-49a8-bced-44922c013e5e | 0.29103
19.73 | 30.46 | 5509.02 | 7.61 | [49.15, 49.15] | [25.08, 25.08] | [8.62, 8.62] | [9.65, 9.65] | 0 | 955.45 | 82.85 | 82.85 | 0 | 7.37 | 89.03 | 62 | 20.3 | 10.73 | 15.54 | 4.19 | 5.77 | 3525.77 | 1041.83 | 1174.65 | 730.78 | 8.59 | 1.55 | 4.51 | 71.89 | 490 | 4700 | 77.16 | 0.47 | 16.19 | 35.2 | 60 | 9 | 9 | 0.64 | 294 | 299.79 | 456209.73 | 456209.73 | 20230204-160652_0e42a183-e08c-4610-b39f-fa7f74843969 | 0
20.24 | 30.76 | 5489.54 | 7.6 | [34.81, 67.44] | [25.02, 3.73] | [9.01, 9.01] | [2.03, 13.36] | 0 | 830.75 | 68.84 | 80.18 | -11.34 | 7.28 | 89.12 | 84 | 18.4 | 10.52 | 16.47 | 3.76 | 6.61 | 3513.31 | 1041.87 | 1211.74 | 738.4 | 5.15 | 1.57 | 4.47 | 73.66 | 490 | 4700 | 75.67 | 0.47 | 13.49 | 25.41 | 60 | 9 | 9 | 0.89 | 294 | 302.02 | 365823.44 | 248533.28 | 20230204-160652_c3b98b40-ab60-425a-bdda-7e718e56c562 | 6.6946
19.16 | 29.66 | 5440.46 | 7.61 | [31.69, 47.08] | [24.95, 14.45] | [8.69, 8.69] | [4.47, 9.36] | 0 | 800.35 | 65.33 | 70.22 | -4.89 | 7.25 | 89.2 | 64 | 18.8 | 10.5 | 14.43 | 4.73 | 6.8 | 3481.89 | 1033.06 | 1208.66 | 733.42 | 6.98 | 1.55 | 4.51 | 68.92 | 490 | 4700 | 75.5 | 0.47 | 13.02 | 36.27 | 60 | 9 | 9 | 0.62 | 294 | 299.62 | 386829.94 | 321233.84 | 20230204-160652_5abd403a-d726-45f8-b7e4-b4cdbe6cc1a9 | 3.7441
19.89 | 30.56 | 5527.21 | 7.6 | [30.61, 51.74] | [25.0, 6.73] | [8.24, 8.24] | [7.41, 10.26] | 0 | 790.7 | 63.85 | 66.71 | -2.86 | 7.24 | 89.08 | 53 | 21.4 | 10.67 | 15.32 | 4.57 | 6.99 | 3537.41 | 1049.11 | 1226.23 | 744.27 | 6.22 | 1.57 | 4.47 | 70.01 | 490 | 4700 | 76.75 | 0.47 | 12.81 | 33.09 | 60 | 9 | 9 | 0.68 | 294 | 300.16 | 415935.49 | 239347.7 | 20230204-160652_4eff511c-025f-4e1b-9331-9f4deb00d65a | 10.0792
19.55 | 30.27 | 5492.03 | 7.6 | [27.32, 54.41] | [25.02, 6.69] | [9.05, 9.05] | [2.02, 10.79] | 0 | 743.86 | 61.39 | 70.15 | -8.76 | 7.22 | 88.93 | 69 | 18.6 | 10.72 | 14.85 | 4.7 | 7.38 | 3514.9 | 1045.39 | 1247.04 | 747.18 | 5.69 | 1.57 | 4.46 | 69.54 | 490 | 4700 | 77.1 | 0.47 | 12.08 | 31.46 | 60 | 9 | 9 | 0.72 | 294 | 300.48 | 359231.2 | 247297.7 | 20230204-160652_4527b027-783a-4a3e-800c-f2dc34ec0830 | 6.3889
20.01 | 30.44 | 5467.64 | 7.61 | [37.4, 56.78] | [24.91, 12.62] | [9.54, 9.54] | [4.18, 11.28] | 0 | 853.55 | 71.85 | 78.94 | -7.09 | 7.31 | 89.34 | 44 | 22.6 | 10.43 | 15.05 | 4.96 | 6.41 | 3499.29 | 1037.78 | 1204.48 | 735.29 | 6.37 | 1.57 | 4.47 | 67.75 | 490 | 4700 | 74.99 | 0.47 | 13.87 | 30.11 | 60 | 9 | 9 | 0.75 | 294 | 300.77 | 389126.51 | 327503.96 | 20230204-160652_c5c6454b-51a1-4fda-aa0d-529316b48465 | 3.5173
19.58 | 30.27 | 5535.77 | 7.48 | [15.41, 43.56] | [25.08, 2.43] | [10.12, 10.12] | [3.14, 8.63] | 0 | 546.29 | 50.61 | 56.11 | -5.5 | 7.1 | 88.8 | 48 | 21 | 10.68 | 14.28 | 5.3 | 10.13 | 3542.89 | 1067.13 | 1398.62 | 789.14 | 5.86 | 1.5 | 4.47 | 66.83 | 490 | 4700 | 76.83 | 0.47 | 8.41 | 39.34 | 60 | 9 | 9 | 0.58 | 294 | 299.18 | 361943.64 | 164507 | 20230204-160652_43d4023c-0c77-4e81-b9d5-c8c178f24cb5 | 11.2692
19.1 | 29.93 | 5491.69 | 7.6 | [26.17, 58.82] | [24.97, 1.95] | [9.14, 9.14] | [2.01, 11.65] | 0 | 728.55 | 60.28 | 69.91 | -9.63 | 7.21 | 88.96 | 66 | 18.5 | 10.83 | 14.4 | 4.71 | 7.54 | 3514.68 | 1046.11 | 1255.27 | 749.26 | 5.17 | 1.56 | 4.48 | 69.71 | 490 | 4700 | 77.86 | 0.47 | 11.91 | 29.14 | 60 | 9 | 9 | 0.78 | 294 | 300.99 | 357584.63 | 201902.01 | 20230204-160652_74f0b3d5-caf9-4b5d-9a08-558e397f3fc9 | 8.886
19.63 | 30.33 | 5515 | 7.49 | [47.96, 47.96] | [25.06, 25.06] | [9.41, 9.41] | [5.61, 5.61] | 0 | 940.87 | 82.43 | 82.43 | 0 | 7.37 | 88.73 | 45 | 22.2 | 10.7 | 14.86 | 4.77 | 5.86 | 3529.6 | 1044.11 | 1185.79 | 734.42 | 14.69 | 1.44 | 4.61 | 69.18 | 490 | 4700 | 76.94 | 0.47 | 15.83 | 60.51 | 60 | 9 | 9 | 0.37 | 294 | 297.37 | 414662.5 | 414662.5 | 20230204-160652_326510b5-793c-4963-82db-7429b7c8d3f9 | 0
18.89 | 29.54 | 5467.74 | 7.6 | [22.33, 45.65] | [25.03, 8.78] | [9.01, 9.01] | [2.0, 9.06] | 0 | 673.51 | 56.37 | 63.44 | -7.07 | 7.17 | 88.98 | 66 | 18.1 | 10.65 | 14.03 | 4.86 | 8.12 | 3499.35 | 1043.64 | 1275 | 751.93 | 6.22 | 1.57 | 4.47 | 68.66 | 490 | 4700 | 76.57 | 0.47 | 10.76 | 37.46 | 60 | 9 | 9 | 0.6 | 294 | 299.44 | 354784.84 | 247684.9 | 20230204-160652_93b80a35-d03b-42cf-8cf3-91bfa591a408 | 6.113
20.11 | 30.63 | 5489.31 | 7.6 | [18.68, 48.92] | [25.07, 1.27] | [7.95, 7.95] | [3.25, 9.69] | 0 | 619.43 | 51.7 | 58.14 | -6.44 | 7.1 | 89.16 | 44 | 22.9 | 10.52 | 15.3 | 4.81 | 8.86 | 3513.16 | 1047.8 | 1292 | 756.25 | 5.33 | 1.6 | 4.41 | 68.62 | 490 | 4700 | 75.67 | 0.47 | 9.63 | 35.04 | 60 | 9 | 9 | 0.65 | 294 | 299.81 | 363816.46 | 163899.96 | 20230204-160652_a2aa0c9a-f8b5-486a-af18-6b7e3297075c | 11.4108
20.63 | 31.4 | 5470.62 | 7.59 | [20.87, 54.55] | [25.05, 0.17] | [10.09, 10.09] | [2.0, 10.8] | 0 | 643.52 | 56.01 | 64.81 | -8.8 | 7.17 | 89.4 | 86 | 17.1 | 10.78 | 15.45 | 5.18 | 8.5 | 3501.2 | 1047.99 | 1309.52 | 761.85 | 5.19 | 1.6 | 4.39 | 67.53 | 490 | 4700 | 77.5 | 0.47 | 10.33 | 31.44 | 60 | 9 | 9 | 0.72 | 294 | 300.48 | 354689.48 | 168491.63 | 20230204-160652_f8fc4306-d166-453b-8e33-a2ee021bbac5 | 10.6277
20.25 | 30.75 | 5532.61 | 7.6 | [21.37, 52.31] | [25.01, 0.8] | [9.05, 9.05] | [3.63, 10.36] | 0 | 658.61 | 55.43 | 62.16 | -6.73 | 7.16 | 88.86 | 46 | 22.2 | 10.5 | 15.01 | 5.24 | 8.4 | 3540.87 | 1056.83 | 1299.1 | 763.07 | 5.35 | 1.6 | 4.39 | 66.7 | 490 | 4700 | 75.49 | 0.47 | 10.2 | 32.78 | 60 | 9 | 9 | 0.69 | 294 | 300.22 | 370214.67 | 168809.57 | 20230204-160652_7992da71-1662-43de-ae95-8d1b6fd30c32 | 11.4957
18.89 | 29.66 | 5492.74 | 7.59 | [25.97, 53.35] | [25.09, 6.3] | [9.13, 9.13] | [2.0, 10.58] | 0 | 724.58 | 60.19 | 68.78 | -8.59 | 7.21 | 89.03 | 68 | 17.8 | 10.77 | 13.99 | 4.9 | 7.58 | 3515.35 | 1046.37 | 1256.61 | 749.61 | 5.69 | 1.55 | 4.49 | 68.74 | 490 | 4700 | 77.45 | 0.47 | 11.77 | 32.1 | 60 | 9 | 9 | 0.71 | 294 | 300.35 | 358849.64 | 239464.58 | 20230204-160652_a922fd44-3964-4aa1-8c28-94ef9c927970 | 6.8142
19.28 | 29.82 | 5437.14 | 7.6 | [49.44, 49.44] | [25.03, 25.03] | [8.25, 8.25] | [6.9, 6.9] | 0 | 960.85 | 82.72 | 82.72 | 0 | 7.37 | 89.17 | 63 | 19.3 | 10.55 | 14.76 | 4.52 | 5.66 | 3479.77 | 1027.77 | 1155.41 | 720.1 | 11.99 | 1.53 | 4.55 | 70 | 490 | 4700 | 75.83 | 0.47 | 16.28 | 49.22 | 60 | 9 | 9 | 0.46 | 294 | 298.14 | 427658.2 | 427658.2 | 20230204-160652_21b5fbc6-6c83-4713-9b12-4d34ca9034c0 | 0
20.46 | 31.59 | 5520.12 | 7.59 | [5.79, 34.68] | [24.98, 0.16] | [9.8, 9.8] | [2.8, 6.87] | 0 | 313.89 | 40.57 | 44.64 | -4.07 | 6.92 | 88.95 | 86 | 16.8 | 11.13 | 15.15 | 5.3 | 17.59 | 3532.88 | 1094.78 | 1740.13 | 871.53 | 5.91 | 1.74 | 4.11 | 67.73 | 490 | 4700 | 80.04 | 0.47 | 4.83 | 49.45 | 60 | 9 | 9 | 0.46 | 294 | 298.12 | 348433.36 | 110693.98 | 20230204-161315_91352dc8-45fd-49f7-87fc-1fac06cdd8b8 | 13.5696
22.12 | 32.36 | 5378.39 | 7.63 | [39.58, 70.96] | [24.8, 5.49] | [7.94, 7.94] | [2.0, 14.07] | 0 | 887.64 | 72.32 | 84.39 | -12.07 | 7.31 | 89.7 | 70 | 22.6 | 10.24 | 18.7 | 3.42 | 6.06 | 3442.17 | 1017.99 | 1160.1 | 716.21 | 5.14 | 1.61 | 4.42 | 74.99 | 490 | 4700 | 73.65 | 0.47 | 14.56 | 24.14 | 60 | 9 | 9 | 0.94 | 294 | 302.44 | 366157.43 | 279350.36 | 20230204-161315_c18632b4-4ec0-4111-9546-4b496a50f4e3 | 4.9547
20.55 | 31.05 | 5457.34 | 7.59 | [15.18, 43.78] | [24.87, 2.95] | [9.67, 9.67] | [2.0, 8.68] | 0 | 545.97 | 49.72 | 56.4 | -6.68 | 7.09 | 89.78 | 79 | 17 | 10.51 | 14.53 | 6.01 | 10 | 3492.7 | 1051.01 | 1371.58 | 775.62 | 5.73 | 1.62 | 4.35 | 63.6 | 490 | 4700 | 75.55 | 0.47 | 8.4 | 39.14 | 60 | 9 | 9 | 0.58 | 294 | 299.21 | 347140.18 | 171157.52 | 20230204-161315_ac5da114-592c-44bf-a45d-3aa379063127 | 10.0447
19.87 | 30.43 | 5496.09 | 7.59 | [23.6, 51.7] | [25.07, 2.47] | [7.29, 7.29] | [4.74, 10.24] | 0 | 704.33 | 55.96 | 61.46 | -5.5 | 7.15 | 89.47 | 81 | 17.8 | 10.56 | 15.54 | 4.34 | 7.8 | 3517.5 | 1044.17 | 1240.26 | 743.82 | 5.46 | 1.56 | 4.47 | 70.89 | 490 | 4700 | 75.92 | 0.47 | 11.16 | 33.15 | 60 | 9 | 9 | 0.68 | 294 | 300.15 | 382673 | 186073.12 | 20230204-161315_337ac0c4-cca7-4eb2-ae61-2531d62b51af | 11.2215
21.04 | 31.68 | 5521.25 | 7.59 | [8.26, 32.73] | [25.05, 1.29] | [8.13, 8.13] | [5.77, 6.49] | 0 | 387.06 | 41.44 | 42.15 | -0.71 | 6.93 | 88.85 | 76 | 19.9 | 10.65 | 16.94 | 4.1 | 14.26 | 3533.6 | 1072.7 | 1523.91 | 813.9 | 6.39 | 1.69 | 4.22 | 72.2 | 490 | 4700 | 76.56 | 0.47 | 5.77 | 52.36 | 60 | 9 | 9 | 0.43 | 294 | 297.89 | 380158.51 | 117552.49 | 20230204-161315_020ccc41-143d-4620-b7f7-e36c202f57e7 | 14.9889
20.13 | 30.91 | 5456.92 | 7.61 | [51.36, 51.36] | [24.93, 24.93] | [9.83, 9.83] | [5.38, 5.38] | 0 | 962.78 | 86.12 | 86.12 | 0 | 7.39 | 89.04 | 82 | 16.7 | 10.78 | 14.59 | 5.54 | 5.67 | 3492.43 | 1033.03 | 1170.53 | 726.26 | 16.02 | 1.56 | 4.49 | 66.06 | 490 | 4700 | 77.54 | 0.47 | 16.61 | 63.18 | 60 | 9 | 9 | 0.36 | 294 | 297.23 | 413975.6 | 413975.6 | 20230204-161315_c9d3decf-a54e-412b-8ef8-74b7809bf909 | 0
20.1 | 30.72 | 5448.46 | 7.6 | [26.43, 59.62] | [24.98, 1.59] | [9.65, 9.65] | [2.02, 11.81] | 0 | 728.3 | 61.06 | 70.86 | -9.8 | 7.22 | 89.32 | 78 | 16.9 | 10.62 | 14.32 | 5.78 | 7.48 | 3487.01 | 1038.78 | 1251.99 | 745.47 | 5.17 | 1.58 | 4.44 | 64.74 | 490 | 4700 | 76.36 | 0.47 | 11.78 | 28.76 | 60 | 9 | 9 | 0.79 | 294 | 301.09 | 358555.42 | 200121.08 | 20230204-161315_c0f709e6-9c3e-497a-add1-63f302d9413a | 9.0431
21.93 | 32.41 | 5393.76 | 7.61 | [64.08, 64.08] | [25.01, 25.01] | [7.89, 7.89] | [3.36, 3.36] | 0 | 1051 | 96.98 | 96.98 | 0 | 7.43 | 89 | 78 | 21.6 | 10.48 | 18.81 | 3.12 | 5.13 | 3452.01 | 1017.61 | 1124.09 | 708.95 | 28.85 | 1.57 | 4.47 | 77.05 | 490 | 4700 | 75.34 | 0.47 | 18.23 | 101.03 | 60 | 9 | 9 | 0.22 | 294 | 296.02 | 403881.16 | 403881.16 | 20230204-161315_44539f67-e12a-4365-a761-45da7ef788f4 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.63 | 31.44 | 5482.06 | 7.6 | [14.24, 43.16] | [24.95, 2.59] | [9.84, 9.84] | [2.0, 8.55] | 0 | 525.32 | 49.03 | 55.59 | -6.56 | 7.08 | 89.29 | 87 | 17 | 10.81 | 15.46 | 5.16 | 10.44 | 3508.52 | 1057.85 | 1399.42 | 784.69 | 5.73 | 1.64 | 4.32 | 67.69 | 490 | 4700 | 77.74 | 0.47 | 8.24 | 39.7 | 60 | 9 | 9 | 0.57 | 294 | 299.13 | 347449.26 | 165084.06 | 20230204-161315_41eeefb3-8790-454e-93c1-b3a04ffe9dd2 | 10.409
19.25 | 30.36 | 5498.05 | 7.6 | [52.27, 80.54] | [24.97, 6.81] | [8.45, 8.45] | [5.85, 15.97] | 0 | 979.17 | 85.69 | 95.8 | -10.11 | 7.38 | 88.85 | 84 | 16.5 | 11.11 | 14.63 | 4.62 | 5.62 | 3518.75 | 1039.12 | 1165.4 | 727.59 | 5.37 | 1.53 | 4.54 | 70.63 | 490 | 4700 | 79.88 | 0.47 | 17.31 | 21.27 | 60 | 9 | 9 | 1.06 | 294 | 303.58 | 418888.97 | 323718.05 | 20230204-161315_90fcb8fb-987a-45e6-86ab-f76005e7639b | 5.4321
20.32 | 31.55 | 5546.05 | 7.59 | [9.55, 36.24] | [24.94, 1.31] | [9.11, 9.11] | [4.13, 7.18] | 0 | 420.06 | 43.6 | 46.66 | -3.06 | 6.98 | 88.17 | 86 | 16 | 11.22 | 14.37 | 5.95 | 13.2 | 3549.47 | 1078.26 | 1517.69 | 817.29 | 6.07 | 1.67 | 4.25 | 65.35 | 490 | 4700 | 80.7 | 0.47 | 6.61 | 47.3 | 60 | 9 | 9 | 0.48 | 294 | 298.31 | 364186 | 128759.89 | 20230204-161315_17c1cd67-cae8-437a-9652-d5c19437b078 | 13.4376
21.57 | 32.37 | 5492.61 | 7.6 | [45.2, 72.17] | [24.95, 5.61] | [8.05, 8.05] | [6.67, 14.31] | 0 | 932.13 | 78.2 | 85.83 | -7.63 | 7.34 | 88.56 | 74 | 21.5 | 10.8 | 18.2 | 3.38 | 5.89 | 3515.27 | 1038.67 | 1173.12 | 728.73 | 5.47 | 1.58 | 4.44 | 76.17 | 490 | 4700 | 77.64 | 0.47 | 15.87 | 23.74 | 60 | 9 | 9 | 0.95 | 294 | 302.58 | 420431.5 | 284501.17 | 20230204-161315_8eee0256-59bc-4ce3-a30a-5382b8e20255 | 7.7586
21.56 | 32.4 | 5464.51 | 7.61 | [56.06, 84.38] | [24.99, 7.55] | [8.44, 8.44] | [5.84, 16.73] | 0 | 1002.83 | 89.49 | 100.37 | -10.88 | 7.4 | 88.28 | 77 | 21.4 | 10.84 | 18.49 | 3.07 | 5.45 | 3497.29 | 1032.29 | 1152.61 | 721.8 | 5.35 | 1.58 | 4.46 | 77.93 | 490 | 4700 | 77.94 | 0.47 | 17.52 | 20.3 | 60 | 9 | 9 | 1.12 | 294 | 304.04 | 422294.12 | 343915.21 | 20230204-161315_5e25c133-a876-4251-b978-b5a07e0a77bd | 4.4737
19.91 | 31.16 | 5543.27 | 7.59 | [23.32, 54.3] | [25.06, 0.84] | [9.38, 9.38] | [4.0, 10.75] | 0 | 685.57 | 57.76 | 64.52 | -6.76 | 7.18 | 88.38 | 86 | 16.5 | 11.26 | 14.86 | 5.05 | 8.09 | 3547.69 | 1058.23 | 1291.52 | 762.47 | 5.37 | 1.58 | 4.42 | 69.05 | 490 | 4700 | 80.96 | 0.47 | 11.43 | 31.58 | 60 | 9 | 9 | 0.72 | 294 | 300.45 | 376598.19 | 175346.21 | 20230204-161315_9307c778-4377-450c-bcb6-c822eb934dd8 | 11.487
21.85 | 32.1 | 5410.46 | 7.6 | [31.42, 63.08] | [25.18, 4.02] | [7.91, 7.91] | [2.0, 12.5] | 0 | 800.59 | 64.51 | 75.01 | -10.5 | 7.24 | 89.35 | 63 | 23.1 | 10.25 | 18.21 | 3.64 | 6.76 | 3462.69 | 1026.05 | 1192.35 | 726.29 | 5.16 | 1.59 | 4.43 | 73.79 | 490 | 4700 | 73.71 | 0.47 | 12.8 | 27.16 | 60 | 9 | 9 | 0.83 | 294 | 301.5 | 363568.98 | 238536.3 | 20230204-161315_74a80635-e644-4046-9984-5c01f8576e73 | 7.1366
20.76 | 31.68 | 5513.36 | 7.6 | [9.56, 39.0] | [25.03, 1.14] | [10.08, 10.08] | [2.17, 7.73] | 0 | 416.9 | 44.67 | 50.22 | -5.55 | 7 | 89.29 | 86 | 17.3 | 10.92 | 15.64 | 5.12 | 13.22 | 3528.55 | 1076.29 | 1542.23 | 822.86 | 5.78 | 1.7 | 4.21 | 68.07 | 490 | 4700 | 78.53 | 0.47 | 6.42 | 43.95 | 60 | 9 | 9 | 0.52 | 294 | 298.64 | 346184.93 | 135461.28 | 20230204-161315_e1290cce-948e-4477-b98c-ec25375053c9 | 12.0276
19.99 | 30.7 | 5439.17 | 7.61 | [35.52, 61.2] | [25.01, 8.11] | [9.6, 9.6] | [3.36, 12.14] | 0 | 833.51 | 70.13 | 78.91 | -8.78 | 7.29 | 89.29 | 77 | 17 | 10.71 | 14.3 | 5.69 | 6.53 | 3481.07 | 1033.03 | 1205.48 | 733.26 | 5.78 | 1.56 | 4.48 | 65.31 | 490 | 4700 | 77.04 | 0.47 | 13.94 | 27.97 | 60 | 9 | 9 | 0.81 | 294 | 301.28 | 380401.67 | 284886.05 | 20230204-161315_20fbdb18-33e5-4e31-bfe1-76df41a7e202 | 5.4518
19.44 | 31.04 | 5523.06 | 7.59 | [44.47, 74.15] | [25.07, 4.61] | [9.41, 9.41] | [5.47, 14.69] | 0 | 914.33 | 78.95 | 88.17 | -9.22 | 7.35 | 88.1 | 86 | 16 | 11.61 | 14.37 | 5.06 | 6.04 | 3534.76 | 1046.33 | 1195.3 | 737.39 | 5.37 | 1.54 | 4.51 | 69.62 | 490 | 4700 | 83.46 | 0.47 | 16.56 | 23.11 | 60 | 9 | 9 | 0.98 | 294 | 302.82 | 410227.83 | 279026.73 | 20230204-161315_d2524044-50c0-471e-9160-5ca0a60c9f8e | 7.4886
21.7 | 32 | 5429.94 | 7.6 | [12.91, 44.37] | [24.81, 0.14] | [8.2, 8.2] | [2.0, 8.78] | 0 | 505.41 | 45.92 | 52.71 | -6.79 | 7.03 | 90.26 | 61 | 23 | 10.3 | 17.84 | 3.85 | 10.74 | 3475.16 | 1044.24 | 1366.91 | 769.65 | 5.23 | 1.65 | 4.31 | 72.77 | 490 | 4700 | 74.06 | 0.47 | 7.6 | 38.65 | 60 | 9 | 9 | 0.59 | 294 | 299.27 | 343096.1 | 137082.14 | 20230204-161315_6230373d-14ce-422d-8422-db746e92b142 | 11.7588
19.3 | 30.09 | 5479.45 | 7.61 | [34.07, 62.56] | [24.99, 3.6] | [8.22, 8.22] | [5.29, 12.4] | 0 | 829.54 | 67.28 | 74.38 | -7.1 | 7.27 | 89.4 | 84 | 16.8 | 10.8 | 14.92 | 4.38 | 6.61 | 3506.85 | 1038.89 | 1201.88 | 734.57 | 5.43 | 1.56 | 4.5 | 71.15 | 490 | 4700 | 77.64 | 0.47 | 13.85 | 27.39 | 60 | 9 | 9 | 0.83 | 294 | 301.44 | 397270.45 | 232158.77 | 20230204-161315_0ef14bcd-df90-453b-922f-49d6953fa13e | 9.4242
21.37 | 32.18 | 5516.81 | 7.59 | [26.06, 53.61] | [25.14, 1.84] | [8.27, 8.27] | [6.37, 10.62] | 0 | 731.33 | 59.47 | 63.72 | -4.25 | 7.19 | 88.5 | 73 | 21.2 | 10.81 | 17.79 | 3.58 | 7.54 | 3530.76 | 1049.08 | 1247.3 | 748.39 | 5.6 | 1.6 | 4.4 | 75.11 | 490 | 4700 | 77.75 | 0.47 | 11.88 | 31.98 | 60 | 9 | 9 | 0.71 | 294 | 300.37 | 403087.97 | 184684.63 | 20230204-161315_db37e0d8-9ac0-4cc2-b48e-c9dca0847f67 | 12.4659
19.81 | 30.97 | 5529.18 | 7.6 | [33.85, 63.5] | [24.85, 2.52] | [9.46, 9.46] | [5.25, 12.58] | 0 | 819.24 | 68.16 | 75.48 | -7.32 | 7.28 | 88.45 | 86 | 16.4 | 11.17 | 14.76 | 5.04 | 6.75 | 3538.68 | 1050.49 | 1229.96 | 746.44 | 5.42 | 1.57 | 4.46 | 68.89 | 490 | 4700 | 80.31 | 0.47 | 13.97 | 26.99 | 60 | 9 | 9 | 0.84 | 294 | 301.55 | 396056.91 | 222684.59 | 20230204-161315_07de088f-9dd3-4dda-97cf-d19eb18679a3 | 9.8957
20.03 | 31.03 | 5504.76 | 7.61 | [46.14, 62.98] | [25.17, 14.79] | [9.81, 9.81] | [6.05, 12.51] | 0 | 923.1 | 81.12 | 87.58 | -6.46 | 7.36 | 88.64 | 85 | 16.7 | 11 | 14.94 | 5.09 | 5.96 | 3523.05 | 1043.01 | 1191.48 | 735.19 | 6.48 | 1.56 | 4.48 | 68.35 | 490 | 4700 | 79.07 | 0.47 | 15.93 | 27.14 | 60 | 9 | 9 | 0.83 | 294 | 301.51 | 419167.71 | 372331.36 | 20230204-161315_47794b0e-b598-4ecd-8308-11c4a9b03d20 | 2.6733
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.7 | 31.14 | 5512.88 | 7.59 | [12.52, 37.34] | [24.9, 2.48] | [8.28, 8.28] | [4.99, 7.4] | 0 | 495.46 | 45.7 | 48.1 | -2.4 | 7.02 | 89.29 | 78 | 18.9 | 10.45 | 16.23 | 4.47 | 11.13 | 3528.24 | 1061.14 | 1398.28 | 784.01 | 6.17 | 1.64 | 4.32 | 70.05 | 490 | 4700 | 75.11 | 0.47 | 7.42 | 45.88 | 60 | 9 | 9 | 0.49 | 294 | 298.44 | 374316.31 | 145648.16 | 20230204-161315_4fac19bf-be0e-4830-b177-06b8b932ab9b | 13.0518
21.66 | 32.24 | 5502.51 | 7.61 | [49.86, 73.44] | [25.18, 13.32] | [8.0, 8.0] | [2.85, 14.58] | 0 | 964.22 | 83.04 | 94.76 | -11.72 | 7.36 | 88.63 | 63 | 22.9 | 10.59 | 18.03 | 3.62 | 5.71 | 3521.61 | 1039.75 | 1166.22 | 727.84 | 5.7 | 1.59 | 4.44 | 74.5 | 490 | 4700 | 76.15 | 0.47 | 16.18 | 23.29 | 60 | 9 | 9 | 0.97 | 294 | 302.75 | 388376.92 | 382888.79 | 20230204-161940_b5aa3c25-f98c-4548-a6bd-aefc752f69df | 0.31325
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.81 | 32.33 | 5503 | 7.59 | [29.57, 61.74] | [25.15, 1.86] | [9.78, 9.78] | [3.35, 12.23] | 0 | 765.15 | 64.5 | 73.38 | -8.88 | 7.25 | 89.03 | 89 | 19.9 | 10.52 | 18.55 | 3.26 | 7.19 | 3521.92 | 1047.78 | 1248.41 | 749.03 | 5.27 | 1.61 | 4.38 | 76.33 | 490 | 4700 | 75.65 | 0.47 | 12.22 | 27.76 | 60 | 9 | 9 | 0.82 | 294 | 301.34 | 376901.9 | 209730.13 | 20230204-161940_669a4f16-6e26-47c3-bd3d-f0b3d1d0b95e | 9.5418
22 | 32.56 | 5511.75 | 7.59 | [22.04, 53.58] | [24.96, 0.54] | [9.55, 9.55] | [3.5, 10.61] | 0 | 666.36 | 56.55 | 63.67 | -7.12 | 7.17 | 89.02 | 83 | 20.8 | 10.56 | 18.68 | 3.32 | 8.27 | 3527.52 | 1053.57 | 1297.81 | 761.7 | 5.33 | 1.63 | 4.33 | 76.07 | 490 | 4700 | 75.95 | 0.47 | 10.44 | 32 | 60 | 9 | 9 | 0.71 | 294 | 300.37 | 369312.89 | 169693.52 | 20230204-161940_1696e315-f61f-4157-9758-68c416da3ba7 | 11.3938
21.62 | 32.22 | 5487.09 | 7.6 | [15.79, 49.24] | [33.49, 3.96] | [10.24, 10.24] | [5.83, 9.76] | 0 | 479.81 | 59.52 | 63.44 | -3.92 | 6.99 | 89.29 | 94 | 19 | 10.6 | 18.27 | 3.35 | 11.44 | 3511.74 | 1054.9 | 1388.42 | 778.02 | 6.1 | 1.66 | 4.28 | 76 | 490 | 4700 | 76.23 | 0.47 | 7.3 | 34.79 | 60 | 9 | 9 | 0.65 | 294 | 299.86 | 492764.95 | 199899.8 | 20230204-161940_5ccf4030-eb78-4992-aaa0-f37b239fc28f | 16.716
21.45 | 32.16 | 5474.1 | 7.6 | [8.44, 43.87] | [34.95, 3.09] | [9.55, 9.55] | [5.12, 8.7] | 0 | 322.8 | 52.94 | 56.51 | -3.57 | 6.85 | 89.28 | 94 | 19.5 | 10.71 | 18.77 | 2.68 | 16.96 | 3503.42 | 1064.71 | 1565.46 | 814.61 | 6.09 | 1.71 | 4.18 | 79.97 | 490 | 4700 | 77.03 | 0.47 | 4.83 | 39.05 | 60 | 9 | 9 | 0.58 | 294 | 299.22 | 496362.54 | 173112.18 | 20230204-161940_8298a46e-ef95-4a25-9f54-4b055c90b1fd | 18.4504
21.92 | 32.47 | 5498.18 | 7.6 | [22.62, 49.2] | [25.02, 4.97] | [9.24, 9.24] | [3.22, 9.76] | 0 | 676.54 | 56.88 | 63.41 | -6.53 | 7.17 | 88.97 | 84 | 20.7 | 10.55 | 18.71 | 3.21 | 8.13 | 3518.84 | 1049.8 | 1284.08 | 756.88 | 5.83 | 1.63 | 4.34 | 76.64 | 490 | 4700 | 75.85 | 0.47 | 10.64 | 34.81 | 60 | 9 | 9 | 0.65 | 294 | 299.85 | 367426.57 | 211249.6 | 20230204-161940_a2738943-0b03-446e-b973-af40f204db84 | 8.9142
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.87 | 32.07 | 5484.42 | 7.6 | [26.74, 58.2] | [25.01, 2.99] | [8.0, 8.0] | [2.09, 11.53] | 0 | 743.91 | 59.75 | 69.19 | -9.44 | 7.2 | 89.36 | 77 | 21.2 | 10.2 | 18.3 | 3.57 | 7.37 | 3510.03 | 1042.06 | 1231.69 | 741.78 | 5.18 | 1.61 | 4.39 | 74.05 | 490 | 4700 | 73.33 | 0.47 | 11.51 | 29.44 | 60 | 9 | 9 | 0.77 | 294 | 300.92 | 358461.6 | 211862.34 | 20230204-161940_71363234-a300-4312-9579-39e8b34096b7 | 8.3675
21.68 | 32.36 | 5493.34 | 7.59 | [14.29, 45.48] | [25.08, 0.89] | [7.67, 7.67] | [2.0, 9.01] | 0 | 535.39 | 47.04 | 54.04 | -7 | 7.03 | 88.64 | 61 | 23 | 10.68 | 17.84 | 3.84 | 10.26 | 3515.74 | 1052.32 | 1343.03 | 768 | 5.22 | 1.63 | 4.33 | 73.56 | 490 | 4700 | 76.8 | 0.47 | 8.29 | 37.7 | 60 | 9 | 9 | 0.6 | 294 | 299.4 | 347141.9 | 149054.22 | 20230204-161940_55fd6eec-b5c6-42ff-94f0-3f6212519031 | 11.3064
21.72 | 32.08 | 5488.16 | 7.61 | [43.03, 73.7] | [24.83, 6.18] | [7.78, 7.78] | [2.6, 14.61] | 0 | 918.36 | 75.64 | 87.66 | -12.02 | 7.33 | 89.36 | 66 | 22.6 | 10.36 | 18.16 | 3.56 | 5.98 | 3512.42 | 1037.86 | 1173.87 | 728.38 | 5.18 | 1.59 | 4.43 | 74.45 | 490 | 4700 | 74.52 | 0.47 | 14.97 | 23.24 | 60 | 9 | 9 | 0.97 | 294 | 302.77 | 375459.2 | 295593.3 | 20230204-161940_7f7d2fa2-4db7-4bfc-a70a-bf94d004b1c4 | 4.5586
22.05 | 32.65 | 5520.46 | 7.6 | [15.42, 41.48] | [25.19, 3.21] | [8.75, 8.75] | [4.14, 8.22] | 0 | 552.16 | 49.36 | 53.44 | -4.08 | 7.07 | 89.57 | 84 | 20.9 | 10.6 | 18.9 | 3.15 | 10 | 3533.09 | 1059.69 | 1360.35 | 776.31 | 6 | 1.66 | 4.28 | 77.09 | 490 | 4700 | 76.23 | 0.47 | 8.47 | 41.3 | 60 | 9 | 9 | 0.55 | 294 | 298.93 | 372154.34 | 166929.66 | 20230204-161940_6bb85cae-d577-4efa-9e80-71e64d32fdac | 11.7137
21.71 | 32.46 | 5453.47 | 7.59 | [2.22, 40.1] | [34.97, 2.43] | [9.12, 9.12] | [2.6, 7.95] | 0 | 159.42 | 46.31 | 51.65 | -5.34 | 6.71 | 89.16 | 91 | 19.6 | 10.75 | 18.5 | 3.21 | 34.21 | 3490.22 | 1104.05 | 2158.35 | 943.05 | 5.83 | 1.86 | 3.87 | 77.01 | 490 | 4700 | 77.33 | 0.47 | 2.33 | 42.73 | 60 | 9 | 9 | 0.53 | 294 | 298.77 | 465304.22 | 153732.35 | 20230204-161940_330582db-8de1-4789-af78-f5c23e0515fd | 17.7838
21.65 | 32.14 | 5458.4 | 7.59 | [7.42, 35.26] | [25.1, 2.25] | [7.91, 7.91] | [2.0, 6.99] | 0 | 363.08 | 40.43 | 45.42 | -4.99 | 6.91 | 88.75 | 62 | 23.3 | 10.49 | 18.25 | 3.4 | 15.03 | 3493.38 | 1062.41 | 1535.76 | 810.74 | 5.79 | 1.7 | 4.2 | 75.55 | 490 | 4700 | 75.43 | 0.47 | 5.38 | 48.59 | 60 | 9 | 9 | 0.47 | 294 | 298.19 | 341538.2 | 136420.29 | 20230204-161940_4e8d8934-b950-42ab-91de-02eab0731f3f | 11.7076
21.76 | 32.25 | 5522.44 | 7.59 | [17.14, 48.87] | [25.03, 0.37] | [8.82, 8.82] | [2.6, 9.68] | 0 | 586.88 | 50.99 | 58.06 | -7.07 | 7.1 | 88.79 | 84 | 20.5 | 10.49 | 18.51 | 3.25 | 9.41 | 3534.36 | 1058.22 | 1337.71 | 771.24 | 5.27 | 1.64 | 4.32 | 76.33 | 490 | 4700 | 75.42 | 0.47 | 8.97 | 35.09 | 60 | 9 | 9 | 0.65 | 294 | 299.81 | 356118.92 | 153453.7 | 20230204-161940_49b0d643-eca4-4310-95e9-df8668edea2c | 11.5676
21.74 | 31.93 | 5505.77 | 7.59 | [13.79, 41.88] | [24.98, 3.11] | [8.97, 8.97] | [2.08, 8.3] | 0 | 519.52 | 47.74 | 53.96 | -6.22 | 7.05 | 89.28 | 89 | 19.4 | 10.18 | 18.06 | 3.69 | 10.6 | 3523.69 | 1060.12 | 1390.61 | 782.91 | 5.75 | 1.65 | 4.29 | 73.41 | 490 | 4700 | 73.22 | 0.47 | 7.63 | 40.9 | 60 | 9 | 9 | 0.55 | 294 | 298.98 | 347420 | 167055.3 | 20230204-161940_b8b608f7-a603-484a-8c2a-a4d159c353b0 | 10.2948
21.5 | 32.33 | 5449.38 | 7.6 | [2.12, 40.47] | [35.05, 2.72] | [8.95, 8.95] | [2.0, 8.02] | 0 | 155.46 | 46.12 | 52.14 | -6.02 | 6.7 | 89 | 92 | 19.1 | 10.83 | 18.13 | 3.37 | 35.05 | 3487.6 | 1103.26 | 2171.28 | 943.96 | 5.75 | 1.87 | 3.86 | 76.24 | 490 | 4700 | 77.85 | 0.47 | 2.29 | 42.34 | 60 | 9 | 9 | 0.53 | 294 | 298.81 | 459860.78 | 158102.22 | 20230204-161940_b098edc8-b0f1-4c75-a2af-7f67c5b1a006 | 17.2237
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.98 | 32.73 | 5526.09 | 7.6 | [16.66, 50.99] | [29.9, 0.69] | [8.91, 8.91] | [4.99, 10.1] | 0 | 529.61 | 55.47 | 60.59 | -5.12 | 7.02 | 88.84 | 83 | 20.6 | 10.74 | 18.48 | 3.5 | 10.43 | 3536.7 | 1058.26 | 1350.49 | 772.01 | 5.49 | 1.66 | 4.29 | 75.43 | 490 | 4700 | 77.25 | 0.47 | 8.19 | 33.63 | 60 | 9 | 9 | 0.67 | 294 | 300.06 | 439813.86 | 163554.43 | 20230204-161940_d0654960-d4a8-4ebf-89e8-4ef79766dafd | 15.7682
21.34 | 32.28 | 5446.34 | 7.6 | [2.25, 40.59] | [34.94, 2.64] | [9.06, 9.06] | [2.0, 8.05] | 0 | 160.1 | 46.25 | 52.29 | -6.04 | 6.71 | 88.97 | 95 | 18.6 | 10.94 | 17.99 | 3.34 | 34.02 | 3485.66 | 1101.66 | 2146.28 | 939.36 | 5.75 | 1.86 | 3.87 | 76.59 | 490 | 4700 | 78.67 | 0.47 | 2.38 | 42.21 | 60 | 9 | 9 | 0.54 | 294 | 298.83 | 458772.76 | 157583.49 | 20230204-161940_24999d64-ae9a-4bf1-9e01-545f40a200af | 17.1912
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 32.66 | 5516.63 | 7.59 | [17.29, 51.14] | [29.99, 0.39] | [9.23, 9.23] | [5.89, 10.13] | 0 | 538.82 | 56.51 | 60.76 | -4.25 | 7.04 | 88.95 | 88 | 20.1 | 10.67 | 18.62 | 3.38 | 10.24 | 3530.64 | 1056.71 | 1347.17 | 770.98 | 5.58 | 1.64 | 4.31 | 75.95 | 490 | 4700 | 76.7 | 0.47 | 8.3 | 33.53 | 60 | 9 | 9 | 0.68 | 294 | 300.08 | 450866.98 | 160576.72 | 20230204-161940_b6524f31-8bbc-4434-a8eb-a220a1e50913 | 16.5691
21.61 | 32.43 | 5450.24 | 7.6 | [2.02, 40.29] | [34.98, 2.69] | [8.92, 8.92] | [2.0, 7.99] | 0 | 152.74 | 45.92 | 51.9 | -5.98 | 6.7 | 89.12 | 90 | 19.6 | 10.82 | 18.38 | 3.23 | 35.68 | 3488.15 | 1104.94 | 2192.84 | 948.73 | 5.75 | 1.88 | 3.84 | 76.99 | 490 | 4700 | 77.83 | 0.47 | 2.24 | 42.52 | 60 | 9 | 9 | 0.53 | 294 | 298.79 | 458873.16 | 157243.13 | 20230204-161940_f791e109-5949-460c-9ee6-75d59a50a7f3 | 17.2163
21.66 | 32.37 | 5516.47 | 7.59 | [38.53, 69.46] | [24.84, 5.3] | [7.85, 7.85] | [2.39, 13.77] | 0 | 878.41 | 71.22 | 82.61 | -11.39 | 7.3 | 88.32 | 62 | 22.9 | 10.71 | 17.89 | 3.77 | 6.28 | 3530.54 | 1044.2 | 1191.53 | 734.9 | 5.17 | 1.58 | 4.43 | 73.98 | 490 | 4700 | 77.01 | 0.47 | 14.59 | 24.66 | 60 | 9 | 9 | 0.92 | 294 | 302.26 | 369572.53 | 272585.62 | 20230204-161940_16b7d7f2-6364-44cd-b718-af28e797449f | 5.5358
21.93 | 32.3 | 5505.23 | 7.6 | [24.91, 56.3] | [25.01, 1.68] | [8.93, 8.93] | [3.1, 11.15] | 0 | 712.27 | 58.85 | 66.91 | -8.06 | 7.19 | 88.77 | 90 | 19.8 | 10.37 | 18.57 | 3.36 | 7.73 | 3523.35 | 1048.94 | 1263 | 751.99 | 5.28 | 1.62 | 4.36 | 75.51 | 490 | 4700 | 74.56 | 0.47 | 11.08 | 30.45 | 60 | 9 | 9 | 0.74 | 294 | 300.69 | 367864.32 | 191084.51 | 20230204-161940_011fb6e1-ac91-412d-8071-8965b7627169 | 10.0902
20.62 | 31.73 | 5463.71 | 7.59 | [6.18, 34.94] | [24.99, 1.15] | [8.9, 8.9] | [2.0, 6.92] | 0 | 325.83 | 40.07 | 44.99 | -4.92 | 6.91 | 88.58 | 97 | 16.9 | 11.1 | 16.54 | 4.09 | 16.77 | 3496.77 | 1075.53 | 1653.29 | 842.72 | 5.79 | 1.71 | 4.16 | 73.08 | 490 | 4700 | 79.84 | 0.47 | 5.06 | 49.06 | 60 | 9 | 9 | 0.46 | 294 | 298.15 | 340031.7 | 122837.97 | 20230204-162602_6cb08677-e976-45ae-87db-f4548b79c838 | 12.3969
22.11 | 32.68 | 5447.2 | 7.6 | [34.98, 66.76] | [24.86, 4.31] | [8.32, 8.32] | [2.0, 13.23] | 0 | 839.67 | 68.16 | 79.39 | -11.23 | 7.28 | 88.28 | 86 | 21 | 10.57 | 19.25 | 2.86 | 6.49 | 3486.21 | 1032.69 | 1192.93 | 729.92 | 5.15 | 1.59 | 4.41 | 78.69 | 490 | 4700 | 75.99 | 0.47 | 13.85 | 25.66 | 60 | 9 | 9 | 0.88 | 294 | 301.94 | 363161.77 | 253034.32 | 20230204-162602_f75dbaf7-3d38-45a0-93cd-f27506314615 | 6.2858
22.14 | 32.49 | 5412.81 | 7.6 | [20.97, 52.63] | [24.95, 1.72] | [8.2, 8.2] | [2.0, 10.43] | 0 | 658.3 | 54.12 | 62.55 | -8.43 | 7.14 | 89.68 | 84 | 21.3 | 10.35 | 19.29 | 2.85 | 8.22 | 3464.2 | 1032.15 | 1257.93 | 742.36 | 5.19 | 1.62 | 4.36 | 78.39 | 490 | 4700 | 74.43 | 0.47 | 10.31 | 32.57 | 60 | 9 | 9 | 0.7 | 294 | 300.26 | 351926.64 | 180331.39 | 20230204-162602_db6e0a5f-c355-4cd8-8129-4f8633a2f92e | 9.7942
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.72 | 31.74 | 5446.45 | 7.6 | [44.64, 69.68] | [25.05, 11.84] | [8.37, 8.37] | [2.0, 13.83] | 0 | 923.99 | 78.06 | 89.89 | -11.83 | 7.34 | 88.13 | 98 | 17.1 | 11.03 | 16.85 | 3.86 | 5.89 | 3485.73 | 1030.45 | 1167.77 | 723.87 | 5.64 | 1.56 | 4.49 | 74.05 | 490 | 4700 | 79.3 | 0.47 | 16.2 | 24.55 | 60 | 9 | 9 | 0.92 | 294 | 302.3 | 374020.77 | 354128.5 | 20230204-162602_1ad30b17-4fbc-4f3e-a995-e7e0ad0ce9a1 | 1.1354
20.37 | 31.54 | 5481.35 | 7.6 | [3.85, 32.91] | [25.18, 0.63] | [8.83, 8.83] | [2.0, 6.52] | 0 | 249.92 | 37.86 | 42.37 | -4.51 | 6.85 | 88.47 | 97 | 16.8 | 11.17 | 16.44 | 3.94 | 21.93 | 3508.06 | 1097.25 | 1874.97 | 896.94 | 5.81 | 1.78 | 4.04 | 73.94 | 490 | 4700 | 80.29 | 0.47 | 3.84 | 52.1 | 60 | 9 | 9 | 0.43 | 294 | 297.91 | 340211.36 | 110525.66 | 20230204-162602_35725284-e655-4bdd-9c7f-64255cac374b | 13.1099
22.25 | 32.68 | 5408.23 | 7.6 | [14.95, 46.83] | [24.93, 0.32] | [8.49, 8.49] | [2.0, 9.27] | 0 | 546.75 | 48.37 | 55.64 | -7.27 | 7.06 | 89.3 | 85 | 21 | 10.42 | 19.12 | 3.13 | 9.89 | 3461.27 | 1037.99 | 1333.17 | 760.34 | 5.22 | 1.64 | 4.31 | 76.9 | 490 | 4700 | 74.96 | 0.47 | 8.43 | 36.62 | 60 | 9 | 9 | 0.62 | 294 | 299.56 | 346623.5 | 146620.56 | 20230204-162602_6402f738-41ad-49a3-925b-08f6a2748f4a | 11.4157
20.54 | 31.14 | 5385.07 | 7.61 | [30.58, 63.17] | [25.14, 3.07] | [8.86, 8.86] | [2.0, 12.52] | 0 | 784.05 | 64.58 | 75.1 | -10.52 | 7.24 | 89.87 | 98 | 16.8 | 10.61 | 16.55 | 3.98 | 6.87 | 3446.44 | 1023.24 | 1203.65 | 727.8 | 5.16 | 1.57 | 4.46 | 72.7 | 490 | 4700 | 76.27 | 0.47 | 13 | 27.13 | 60 | 9 | 9 | 0.83 | 294 | 301.51 | 363145.03 | 227890.84 | 20230204-162602_8f298c37-cf64-402d-94f8-78d928747063 | 7.72
20.05 | 31.44 | 5485.65 | 7.59 | [22.82, 55.53] | [24.81, 1.09] | [9.36, 9.36] | [2.0, 11.0] | 0 | 681.09 | 56.99 | 65.98 | -8.99 | 7.18 | 88.08 | 97 | 16.9 | 11.39 | 16.54 | 3.51 | 8.05 | 3510.82 | 1047.59 | 1281.6 | 755.48 | 5.18 | 1.58 | 4.43 | 76.44 | 490 | 4700 | 81.93 | 0.47 | 11.61 | 30.88 | 60 | 9 | 9 | 0.73 | 294 | 300.6 | 352751.1 | 182017.23 | 20230204-162602_6ee43f9d-1c3f-490d-a050-08ec37dfcaeb | 9.7451
21.98 | 32.43 | 5409.16 | 7.61 | [34.43, 66.71] | [25.15, 4.09] | [8.52, 8.52] | [2.0, 13.22] | 0 | 829.08 | 68.1 | 79.32 | -11.22 | 7.27 | 89.43 | 85 | 21 | 10.45 | 19.12 | 2.86 | 6.52 | 3461.86 | 1025.93 | 1189.19 | 726 | 5.15 | 1.59 | 4.42 | 78.5 | 490 | 4700 | 75.12 | 0.47 | 13.6 | 25.68 | 60 | 9 | 9 | 0.88 | 294 | 301.93 | 366381.98 | 250395.57 | 20230204-162602_90ef631e-a868-43ff-9ee3-a9d271025600 | 6.6202
22.33 | 32.87 | 5447.17 | 7.6 | [19.24, 51.05] | [25.05, 1.35] | [8.27, 8.27] | [2.0, 10.11] | 0 | 627.66 | 52.56 | 60.67 | -8.11 | 7.12 | 89.18 | 80 | 22 | 10.54 | 19.45 | 2.88 | 8.68 | 3486.19 | 1040.18 | 1283.28 | 751.23 | 5.2 | 1.63 | 4.34 | 78.51 | 490 | 4700 | 75.76 | 0.47 | 9.87 | 33.58 | 60 | 9 | 9 | 0.67 | 294 | 300.07 | 351619.23 | 171324.06 | 20230204-162602_99045306-03a0-4762-9b7c-0c8277dbc925 | 10.2908
21.61 | 32.41 | 5437.61 | 7.6 | [39.09, 71.74] | [25.19, 4.76] | [8.8, 8.8] | [2.0, 14.22] | 0 | 871.94 | 73.08 | 85.3 | -12.22 | 7.31 | 88.61 | 90 | 19.7 | 10.8 | 18.47 | 3.14 | 6.24 | 3480.07 | 1030.5 | 1184.19 | 727.34 | 5.14 | 1.58 | 4.44 | 77.5 | 490 | 4700 | 77.68 | 0.47 | 14.83 | 23.88 | 60 | 9 | 9 | 0.95 | 294 | 302.53 | 371207.69 | 273422.79 | 20230204-162602_f6a6d0fb-a0f1-4555-93d1-4688dd52685a | 5.5813
21.86 | 32.49 | 5414.52 | 7.61 | [40.17, 72.17] | [24.81, 5.12] | [8.54, 8.54] | [2.0, 14.3] | 0 | 888.12 | 73.52 | 85.83 | -12.31 | 7.32 | 89 | 85 | 20.5 | 10.63 | 18.64 | 3.23 | 6.1 | 3465.29 | 1025.54 | 1173.07 | 722.7 | 5.14 | 1.58 | 4.44 | 76.7 | 490 | 4700 | 76.41 | 0.47 | 14.99 | 23.74 | 60 | 9 | 9 | 0.95 | 294 | 302.58 | 367182.37 | 278787.38 | 20230204-162602_55c4c123-e1f6-47b3-9608-d1900a8c47f8 | 5.0454
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.32 | 32.75 | 5392.16 | 7.61 | [31.14, 63.2] | [24.88, 3.35] | [8.59, 8.59] | [2.0, 12.52] | 0 | 795.62 | 64.61 | 75.14 | -10.53 | 7.25 | 89.58 | 79 | 22 | 10.43 | 19.32 | 3 | 6.78 | 3450.98 | 1023.93 | 1198.89 | 727.07 | 5.16 | 1.6 | 4.4 | 77.67 | 490 | 4700 | 75.02 | 0.47 | 12.98 | 27.12 | 60 | 9 | 9 | 0.83 | 294 | 301.51 | 360275.16 | 231182.86 | 20230204-162602_68e631f7-fe63-4606-be36-47dc9a792f90 | 7.3683
22.14 | 32.72 | 5441.78 | 7.6 | [19.46, 51.35] | [25.06, 1.33] | [8.35, 8.35] | [2.0, 10.17] | 0 | 630.82 | 52.87 | 61.03 | -8.16 | 7.12 | 88.34 | 89 | 20.4 | 10.58 | 19.04 | 3.1 | 8.63 | 3482.74 | 1039.19 | 1281.57 | 750.49 | 5.2 | 1.62 | 4.35 | 77.34 | 490 | 4700 | 76.07 | 0.47 | 9.97 | 33.39 | 60 | 9 | 9 | 0.68 | 294 | 300.1 | 351954.99 | 171972.99 | 20230204-162602_432aac77-3e85-4667-84ed-4536c19bc1a3 | 10.2729
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.29 | 32.17 | 5456.16 | 7.6 | [29.85, 61.97] | [24.82, 2.99] | [8.71, 8.71] | [1.99, 12.28] | 0 | 780.29 | 63.38 | 73.67 | -10.29 | 7.24 | 88.79 | 95 | 18.7 | 10.88 | 18.09 | 3.19 | 6.99 | 3491.94 | 1036.81 | 1220.54 | 737.61 | 5.16 | 1.59 | 4.43 | 77.32 | 490 | 4700 | 78.27 | 0.47 | 13.06 | 27.66 | 60 | 9 | 9 | 0.82 | 294 | 301.37 | 358439.07 | 223359.19 | 20230204-162602_ebe99646-f5e2-422b-98da-f07c1bd2b4c9 | 7.71
20.97 | 31.84 | 5468.45 | 7.6 | [28.49, 61.56] | [25.14, 2.27] | [9.34, 9.34] | [2.0, 12.19] | 0 | 755.28 | 62.97 | 73.17 | -10.2 | 7.23 | 88.92 | 97 | 18.1 | 10.88 | 17.74 | 3.23 | 7.24 | 3499.81 | 1040.88 | 1239.76 | 743.74 | 5.16 | 1.59 | 4.42 | 77.1 | 490 | 4700 | 78.21 | 0.47 | 12.53 | 27.85 | 60 | 9 | 9 | 0.81 | 294 | 301.32 | 361777.41 | 213858.47 | 20230204-162602_f7f0ce25-407c-4b30-968e-a967772b3d1d | 8.4429
20.34 | 31 | 5382.27 | 7.61 | [11.23, 39.34] | [24.91, 2.6] | [8.74, 8.74] | [2.0, 7.8] | 0 | 463.3 | 44.88 | 50.68 | -5.8 | 7.01 | 89.81 | 98 | 16.6 | 10.66 | 16.35 | 3.99 | 11.62 | 3444.65 | 1040.41 | 1409.57 | 777.04 | 5.76 | 1.64 | 4.33 | 72.79 | 490 | 4700 | 76.68 | 0.47 | 7.22 | 43.56 | 60 | 9 | 9 | 0.52 | 294 | 298.68 | 343258.46 | 153185.35 | 20230204-162602_59b604ee-f80e-429e-9f33-a8d2fe874ab9 | 10.8489
22.35 | 32.78 | 5416.79 | 7.6 | [18.08, 49.99] | [24.98, 0.97] | [8.44, 8.44] | [2.0, 9.9] | 0 | 606.79 | 51.5 | 59.4 | -7.9 | 7.11 | 89.45 | 80 | 22 | 10.43 | 19.45 | 2.9 | 8.93 | 3466.75 | 1035.92 | 1292.2 | 751.16 | 5.2 | 1.63 | 4.33 | 78.24 | 490 | 4700 | 74.98 | 0.47 | 9.46 | 34.3 | 60 | 9 | 9 | 0.66 | 294 | 299.94 | 349853.27 | 163731.27 | 20230204-162602_80f6217c-e0f0-4c1a-b291-b25f8547d817 | 10.6234
20.49 | 31.34 | 5391.97 | 7.61 | [47.19, 47.19] | [24.97, 24.97] | [9.1, 9.1] | [2.0, 2.0] | 0 | 938.65 | 81.26 | 81.26 | 0 | 7.36 | 88.87 | 98 | 17.1 | 10.85 | 16.85 | 3.64 | 5.74 | 3450.86 | 1020.61 | 1157.99 | 717.56 | 40.62 | 1.55 | 4.5 | 74.9 | 490 | 4700 | 78.04 | 0.47 | 16.45 | 169.74 | 60 | 9 | 9 | 0.13 | 294 | 295.2 | 375874.47 | 375874.47 | 20230204-162602_b4176341-9e94-4677-8a3b-64dc122428ec | 0
20.25 | 31.35 | 5479.53 | 7.61 | [25.42, 57.73] | [25.06, 2.2] | [8.69, 8.69] | [2.0, 11.44] | 0 | 720.44 | 59.17 | 68.62 | -9.45 | 7.19 | 88.93 | 97 | 17.3 | 11.1 | 16.94 | 3.31 | 7.61 | 3506.9 | 1043.24 | 1249.8 | 746.44 | 5.17 | 1.59 | 4.43 | 77.01 | 490 | 4700 | 79.83 | 0.47 | 12.08 | 29.69 | 60 | 9 | 9 | 0.76 | 294 | 300.86 | 357590.11 | 201323.49 | 20230204-162602_99be4bf4-0735-420d-b4ff-792e3783208c | 8.9193
22.26 | 32.89 | 5467.07 | 7.6 | [20.81, 52.67] | [24.95, 1.53] | [8.4, 8.4] | [2.0, 10.43] | 0 | 654.34 | 54.16 | 62.6 | -8.44 | 7.14 | 88.58 | 78 | 22 | 10.63 | 19.19 | 3.07 | 8.36 | 3498.92 | 1043.12 | 1275.91 | 751.35 | 5.19 | 1.63 | 4.35 | 77.59 | 490 | 4700 | 76.47 | 0.47 | 10.4 | 32.55 | 60 | 9 | 9 | 0.7 | 294 | 300.26 | 351963.65 | 178246.94 | 20230204-162602_1682a359-b710-4c8c-b165-638bbb24d498 | 9.9153
20.53 | 31.72 | 5474.89 | 7.6 | [15.32, 43.97] | [24.98, 3.04] | [9.64, 9.64] | [2.0, 8.72] | 0 | 547.92 | 49.94 | 56.65 | -6.71 | 7.09 | 88.32 | 98 | 17 | 11.18 | 16.75 | 3.78 | 9.99 | 3503.93 | 1054.04 | 1372.89 | 777.25 | 5.73 | 1.63 | 4.33 | 74.74 | 490 | 4700 | 80.42 | 0.47 | 8.94 | 38.96 | 60 | 9 | 9 | 0.58 | 294 | 299.23 | 348495.85 | 172774.98 | 20230204-162602_8e4c90e8-c938-4dbc-85f2-1b8b57d6a6ed | 10.0297
22.29 | 32.75 | 5419.38 | 7.6 | [39.68, 65.38] | [25.12, 10.4] | [8.56, 8.56] | [2.0, 12.97] | 0 | 879.97 | 73.36 | 84.34 | -10.98 | 7.31 | 89.07 | 85 | 20.8 | 10.46 | 18.93 | 3.36 | 6.16 | 3468.4 | 1026.56 | 1175.74 | 723.67 | 5.65 | 1.58 | 4.43 | 75.71 | 490 | 4700 | 75.22 | 0.47 | 14.58 | 26.17 | 60 | 9 | 9 | 0.86 | 294 | 301.78 | 370717.56 | 324122.64 | 20230204-162602_4e869081-fd05-470c-99e3-3f4cf39634b1 | 2.6595
22.21 | 32.67 | 5411.83 | 7.6 | [3.36, 31.25] | [25.17, 1.47] | [10.62, 10.62] | [2.0, 6.19] | 0 | 236.12 | 39.15 | 43.34 | -4.19 | 6.89 | 90.14 | 96 | 19.5 | 10.45 | 19.01 | 3.2 | 22.92 | 3463.57 | 1103.38 | 2017.71 | 934.52 | 6.32 | 1.85 | 3.9 | 76.56 | 490 | 4700 | 75.17 | 0.47 | 3.43 | 54.84 | 60 | 9 | 9 | 0.41 | 294 | 297.72 | 341230.97 | 117658.6 | 20230204-163228_9cadf07f-d77d-4cf3-9589-b1c2fd0c30fa | 12.761
22.19 | 32.74 | 5471.25 | 7.59 | [23.35, 56.47] | [25.01, 1.07] | [9.56, 9.56] | [2.0, 11.18] | 0 | 685.4 | 57.92 | 67.1 | -9.18 | 7.19 | 88.76 | 85 | 20.4 | 10.55 | 18.54 | 3.65 | 7.98 | 3501.6 | 1044.88 | 1277.7 | 753.5 | 5.18 | 1.62 | 4.35 | 74.32 | 490 | 4700 | 75.87 | 0.47 | 10.87 | 30.36 | 60 | 9 | 9 | 0.75 | 294 | 300.71 | 355921.6 | 184613.07 | 20230204-163228_d4aac477-4f9f-441e-9337-757c6a96df4a | 9.7779
21.94 | 32.26 | 5440.8 | 7.61 | [30.92, 57.42] | [24.98, 7.87] | [8.75, 8.75] | [2.0, 11.39] | 0 | 790.6 | 64.65 | 74.04 | -9.39 | 7.25 | 89.72 | 76 | 21.8 | 10.32 | 18.74 | 3.2 | 6.88 | 3482.11 | 1033.53 | 1213 | 734.54 | 5.68 | 1.61 | 4.4 | 76.34 | 490 | 4700 | 74.23 | 0.47 | 12.62 | 29.81 | 60 | 9 | 9 | 0.76 | 294 | 300.83 | 361435.75 | 270258.43 | 20230204-163228_f4d9136d-7c5f-4115-bed5-81e02ade9b44 | 5.2042
21.76 | 33.09 | 5562.95 | 7.59 | [8.96, 35.78] | [25.02, 0.42] | [9.85, 9.85] | [4.87, 7.09] | 0 | 402.3 | 43.83 | 46.05 | -2.22 | 6.99 | 88.47 | 89 | 18.9 | 11.32 | 17.56 | 4.2 | 13.83 | 3560.29 | 1087.08 | 1572.12 | 833.7 | 6.19 | 1.71 | 4.16 | 72.95 | 490 | 4700 | 81.42 | 0.47 | 6.35 | 47.92 | 60 | 9 | 9 | 0.47 | 294 | 298.25 | 372832.36 | 117147.16 | 20230204-163228_44f0f0bd-fd82-44c2-9d63-55e7a60fb289 | 14.5939
21.73 | 32.96 | 5499.13 | 7.61 | [50.58, 50.58] | [25.07, 25.07] | [9.94, 9.94] | [4.18, 4.18] | 0 | 955.17 | 85.59 | 85.59 | 0 | 7.38 | 88.24 | 71 | 22.2 | 11.23 | 18.46 | 3.27 | 5.76 | 3519.44 | 1041.28 | 1182.15 | 732.54 | 20.49 | 1.6 | 4.42 | 77.45 | 490 | 4700 | 80.72 | 0.47 | 16.97 | 81.31 | 60 | 9 | 9 | 0.28 | 294 | 296.51 | 402876.72 | 402876.72 | 20230204-163228_392e2257-671b-4dee-85c8-35d8b238f46b | 0
21.56 | 33.06 | 5573.23 | 7.6 | [19.96, 43.5] | [24.84, 2.51] | [10.02, 10.02] | [7.4, 8.62] | 0 | 631.4 | 54.82 | 56.03 | -1.21 | 7.16 | 88.18 | 90 | 18.8 | 11.5 | 17.59 | 3.98 | 8.83 | 3566.87 | 1068.4 | 1342.29 | 778.19 | 6.36 | 1.65 | 4.31 | 74.31 | 490 | 4700 | 82.71 | 0.47 | 10.57 | 39.39 | 60 | 9 | 9 | 0.57 | 294 | 299.17 | 406140.71 | 165316.46 | 20230204-163228_1d886f71-5eac-4070-a368-052da601ac6c | 13.7457
22.11 | 32.49 | 5403.29 | 7.61 | [26.4, 60.52] | [25.02, 0.88] | [10.51, 10.51] | [2.0, 11.99] | 0 | 721.56 | 61.93 | 71.91 | -9.98 | 7.23 | 90.44 | 85 | 20.1 | 10.38 | 18.25 | 3.87 | 7.49 | 3458.11 | 1031.92 | 1255.45 | 743.48 | 5.17 | 1.62 | 4.36 | 72.86 | 490 | 4700 | 74.61 | 0.47 | 11.5 | 28.33 | 60 | 9 | 9 | 0.8 | 294 | 301.19 | 359473.49 | 194874.73 | 20230204-163228_5af75082-cda2-4678-a54d-ff0127ab1b83 | 9.3949
22.15 | 32.8 | 5466.11 | 7.6 | [34.31, 60.37] | [24.99, 8.9] | [8.59, 8.59] | [2.0, 11.98] | 0 | 829.11 | 67.89 | 77.86 | -9.97 | 7.27 | 88.39 | 77 | 22.2 | 10.65 | 19.25 | 2.9 | 6.59 | 3498.31 | 1036.89 | 1202.91 | 734.03 | 5.67 | 1.6 | 4.4 | 78.58 | 490 | 4700 | 76.58 | 0.47 | 13.69 | 28.35 | 60 | 9 | 9 | 0.8 | 294 | 301.19 | 364446.66 | 291331.25 | 20230204-163228_e4972e1b-d56c-4881-86fe-46218ff5ef74 | 4.1733
22.18 | 32.62 | 5430.54 | 7.59 | [3.25, 30.4] | [24.91, 1.79] | [9.98, 9.98] | [2.0, 6.02] | 0 | 232.52 | 38.14 | 42.17 | -4.03 | 6.87 | 90.45 | 81 | 21.4 | 10.45 | 19 | 3.17 | 23.36 | 3475.55 | 1104.26 | 2009.16 | 931.53 | 6.33 | 1.84 | 3.91 | 76.7 | 490 | 4700 | 75.12 | 0.47 | 3.36 | 56.37 | 60 | 9 | 9 | 0.4 | 294 | 297.61 | 337456.22 | 118528.84 | 20230204-163228_961034e0-fa5a-4d68-a862-515841e08b48 | 12.4959
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.19 | 32.69 | 5399.92 | 7.6 | [20.56, 52.75] | [24.89, 0.79] | [9.14, 9.14] | [2.35, 10.45] | 0 | 646.18 | 54.59 | 62.68 | -8.09 | 7.15 | 90.08 | 95 | 18.9 | 10.5 | 18.29 | 3.9 | 8.36 | 3455.95 | 1032.39 | 1277.09 | 747.16 | 5.23 | 1.63 | 4.35 | 72.93 | 490 | 4700 | 75.52 | 0.47 | 10.27 | 32.51 | 60 | 9 | 9 | 0.7 | 294 | 300.27 | 355118.11 | 170073.65 | 20230204-163228_b4cd858d-cbe2-462f-b0a3-1e74a4df1bca | 10.5619
21.5 | 33.03 | 5566.33 | 7.6 | [42.83, 68.87] | [25.18, 3.04] | [9.96, 9.96] | [9.75, 13.64] | 0 | 895.6 | 77.97 | 81.87 | -3.9 | 7.34 | 87.71 | 90 | 19 | 11.53 | 17.78 | 3.71 | 6.22 | 3562.45 | 1055.61 | 1214.67 | 745.93 | 5.71 | 1.6 | 4.4 | 75.64 | 490 | 4700 | 82.95 | 0.47 | 15.9 | 24.89 | 60 | 9 | 9 | 0.91 | 294 | 302.19 | 454093.98 | 244998.58 | 20230204-163228_6d69ac3d-5298-427f-9cd3-2d5b0d1ca158 | 11.9347
21.77 | 32.64 | 5438.01 | 7.62 | [55.67, 75.71] | [24.95, 11.58] | [10.36, 10.36] | [8.36, 15.02] | 0 | 986.01 | 90.98 | 97.65 | -6.67 | 7.41 | 89.39 | 94 | 18.6 | 10.87 | 17.87 | 3.9 | 5.52 | 3480.33 | 1029.35 | 1163.51 | 723.26 | 6.06 | 1.6 | 4.43 | 73.6 | 490 | 4700 | 78.17 | 0.47 | 17.31 | 22.6 | 60 | 9 | 9 | 1 | 294 | 303.01 | 448826.7 | 370035.68 | 20230204-163228_6f48bf9a-3fb6-48df-8f49-6f2209e4b3af | 4.4972
22.27 | 33.2 | 5498.56 | 7.6 | [5.14, 32.24] | [25.06, 2.31] | [10.19, 10.19] | [2.03, 6.39] | 0 | 293.23 | 40.39 | 44.74 | -4.35 | 6.92 | 90.25 | 87 | 19.7 | 10.93 | 18.1 | 4.16 | 18.75 | 3519.08 | 1098.04 | 1808.34 | 887.86 | 6.32 | 1.8 | 4 | 72.43 | 490 | 4700 | 78.63 | 0.47 | 4.43 | 53.13 | 60 | 9 | 9 | 0.43 | 294 | 297.83 | 341422.39 | 130392.66 | 20230204-163228_05325a78-0675-4039-8882-cffcc3b78bc6 | 12.0451
21.99 | 33.17 | 5519.67 | 7.59 | [5.27, 31.63] | [24.77, 2.27] | [9.98, 9.98] | [2.42, 6.27] | 0 | 299.4 | 40.02 | 43.88 | -3.86 | 6.92 | 88.1 | 75 | 21.9 | 11.18 | 18.7 | 3.29 | 18.44 | 3532.59 | 1100.03 | 1792.73 | 885.39 | 6.39 | 1.78 | 4.02 | 77.28 | 490 | 4700 | 80.41 | 0.47 | 4.61 | 54.17 | 60 | 9 | 9 | 0.42 | 294 | 297.76 | 341700 | 127971.37 | 20230204-163228_c57d0b80-8e56-42bc-8721-1c36d262d6ef | 12.1991
21.96 | 32.55 | 5473.42 | 7.6 | [41.8, 41.8] | [25.04, 25.04] | [8.76, 8.76] | [2.0, 2.0] | 0 | 897.8 | 75.6 | 75.6 | 0 | 7.33 | 88.44 | 75 | 22.2 | 10.59 | 18.99 | 2.97 | 6.1 | 3502.99 | 1036.63 | 1184.21 | 730.27 | 37.74 | 1.59 | 4.42 | 78.09 | 490 | 4700 | 76.15 | 0.47 | 14.94 | 169.49 | 60 | 9 | 9 | 0.13 | 294 | 295.2 | 371759.04 | 371759.04 | 20230204-163228_b5a51695-f7fc-43bc-b477-c4f3e78d5541 | 0
22.02 | 32.39 | 5441.69 | 7.6 | [44.99, 44.99] | [24.99, 24.99] | [8.31, 8.31] | [2.0, 2.0] | 0 | 927.94 | 78.29 | 78.29 | 0 | 7.34 | 89.29 | 77 | 21.8 | 10.37 | 18.87 | 3.15 | 5.86 | 3482.68 | 1029.41 | 1165.35 | 722.88 | 39.15 | 1.58 | 4.44 | 76.7 | 490 | 4700 | 74.59 | 0.47 | 15.33 | 169.81 | 60 | 9 | 9 | 0.13 | 294 | 295.2 | 373532.18 | 373532.18 | 20230204-163228_34a68c8f-5108-4dd4-9e08-83271423bc71 | 0
21.94 | 33.22 | 5532.03 | 7.6 | [25.01, 57.49] | [25.13, 0.57] | [10.25, 10.25] | [3.47, 11.38] | 0 | 703.21 | 60.39 | 68.31 | -7.92 | 7.21 | 87.91 | 72 | 22.2 | 11.28 | 18.59 | 3.35 | 7.87 | 3540.5 | 1056.85 | 1291.14 | 762.35 | 5.3 | 1.63 | 4.34 | 77.09 | 490 | 4700 | 81.08 | 0.47 | 11.81 | 29.83 | 60 | 9 | 9 | 0.76 | 294 | 300.83 | 374372.22 | 181985.34 | 20230204-163228_cc6641b5-feb8-4e28-8b26-7e4531ffb807 | 10.981
22.38 | 33.13 | 5480.04 | 7.6 | [28.06, 61.94] | [24.95, 1.34] | [10.33, 10.33] | [2.0, 12.27] | 0 | 745.03 | 63.34 | 73.61 | -10.27 | 7.24 | 89 | 87 | 20 | 10.75 | 18.4 | 3.98 | 7.36 | 3507.23 | 1045.26 | 1259.8 | 750.55 | 5.16 | 1.63 | 4.35 | 72.97 | 490 | 4700 | 77.31 | 0.47 | 12.16 | 27.68 | 60 | 9 | 9 | 0.82 | 294 | 301.36 | 359855.34 | 204374.02 | 20230204-163228_8e3e2b9d-9802-44f5-9363-e1daa40f923d | 8.8745
21.94 | 32.55 | 5407.96 | 7.62 | [48.3, 48.3] | [25.16, 25.16] | [10.29, 10.29] | [2.03, 2.03] | 0 | 935.53 | 83.75 | 83.75 | 0 | 7.37 | 89.98 | 69 | 22.6 | 10.61 | 18.57 | 3.37 | 5.78 | 3461.09 | 1024.82 | 1170.39 | 722.49 | 41.32 | 1.6 | 4.43 | 75.9 | 490 | 4700 | 76.33 | 0.47 | 15.97 | 167.53 | 60 | 9 | 9 | 0.14 | 294 | 295.22 | 380443.11 | 380443.11 | 20230204-163228_567ee266-6182-44d0-ba87-68d0b96308dd | 0
21.94 | 32.6 | 5409.17 | 7.61 | [39.62, 69.57] | [25.15, 3.61] | [9.53, 9.53] | [5.38, 13.78] | 0 | 871.56 | 74.3 | 82.71 | -8.41 | 7.32 | 89.92 | 94 | 18.7 | 10.65 | 17.97 | 3.97 | 6.21 | 3461.87 | 1026.03 | 1184.71 | 725.68 | 5.39 | 1.59 | 4.43 | 72.86 | 490 | 4700 | 76.61 | 0.47 | 14.72 | 24.63 | 60 | 9 | 9 | 0.92 | 294 | 302.27 | 406121.15 | 253589.79 | 20230204-163228_ab778cfe-e213-44de-aaf0-af4f25431fe8 | 8.7061
21.76 | 32.7 | 5458 | 7.61 | [59.4, 59.4] | [24.81, 24.81] | [10.05, 10.05] | [3.33, 3.33] | 0 | 1011.66 | 94.26 | 94.26 | 0 | 7.43 | 89.02 | 70 | 22.5 | 10.94 | 18.61 | 3.15 | 5.4 | 3493.12 | 1032.31 | 1159.49 | 723.75 | 28.35 | 1.59 | 4.44 | 77.64 | 490 | 4700 | 78.69 | 0.47 | 17.9 | 102.11 | 60 | 9 | 9 | 0.22 | 294 | 296 | 398882.54 | 398882.54 | 20230204-163228_7d42abf7-549f-4481-94b0-d74d24357abe | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.06 | 32.4 | 5460.58 | 7.6 | [19.37, 51.24] | [25.01, 1.29] | [8.37, 8.37] | [2.0, 10.15] | 0 | 629.8 | 52.75 | 60.9 | -8.15 | 7.12 | 89.29 | 82 | 20.7 | 10.34 | 18.45 | 3.61 | 8.67 | 3494.77 | 1042.92 | 1287.28 | 753.45 | 5.2 | 1.63 | 4.35 | 74.14 | 490 | 4700 | 74.33 | 0.47 | 9.69 | 33.46 | 60 | 9 | 9 | 0.68 | 294 | 300.09 | 351283.43 | 171142.05 | 20230204-163228_232f0df2-d2fd-4d6a-9561-76ac96f8409f | 10.282
21.57 | 32.83 | 5497.93 | 7.61 | [67.78, 67.78] | [24.93, 24.93] | [10.3, 10.3] | [9.9, 9.9] | 0 | 1051.71 | 103.01 | 103.01 | 0 | 7.46 | 88.5 | 91 | 19.3 | 11.26 | 18.2 | 3.36 | 5.23 | 3518.68 | 1039.1 | 1159.08 | 726.91 | 10.4 | 1.58 | 4.45 | 76.99 | 490 | 4700 | 80.97 | 0.47 | 19.15 | 34.3 | 60 | 9 | 9 | 0.66 | 294 | 299.94 | 474788.57 | 474788.57 | 20230204-163228_ef90db46-46d1-4da8-8236-3e2a514ce119 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.47 | 32.02 | 5434.1 | 7.61 | [34.92, 68.76] | [24.95, 2.32] | [10.64, 10.64] | [2.41, 13.62] | 0 | 820.25 | 70.51 | 81.72 | -11.21 | 7.3 | 89.97 | 89 | 20.2 | 10.55 | 18.84 | 2.63 | 6.62 | 3477.82 | 1033.93 | 1219.63 | 737.11 | 5.18 | 1.6 | 4.41 | 80.08 | 490 | 4700 | 75.88 | 0.47 | 13.49 | 24.93 | 60 | 9 | 9 | 0.91 | 294 | 302.17 | 370460.15 | 236456.29 | 20230204-163852_8ad59907-34b7-4839-9946-9cfea0696c68 | 7.6486
21.98 | 32.29 | 5435.18 | 7.6 | [14.2, 43.99] | [24.99, 1.92] | [10.74, 10.74] | [2.0, 8.72] | 0 | 520.05 | 49.93 | 56.65 | -6.72 | 7.09 | 90.48 | 91 | 19.9 | 10.31 | 18.79 | 3.19 | 10.45 | 3478.52 | 1051.88 | 1411.53 | 785.33 | 5.73 | 1.67 | 4.25 | 76.39 | 490 | 4700 | 74.14 | 0.47 | 7.84 | 38.96 | 60 | 9 | 9 | 0.58 | 294 | 299.23 | 348616.45 | 160007.01 | 20230204-163852_a0238ab2-eec5-4580-a9b7-395b2a5cf700 | 10.7654
21.87 | 32.48 | 5382.39 | 7.6 | [45.39, 69.82] | [14.97, 2.32] | [10.85, 10.85] | [2.04, 13.83] | 0 | 1034.76 | 71.21 | 82.99 | -11.78 | 7.52 | 91.42 | 69 | 21.8 | 10.62 | 17.83 | 4.04 | 5.2 | 3444.73 | 1022.41 | 1173.53 | 723.78 | 5.15 | 1.58 | 4.45 | 72.43 | 490 | 4700 | 76.35 | 0.47 | 18.17 | 24.55 | 60 | 9 | 9 | 0.92 | 294 | 302.3 | 253523.27 | 239678.44 | 20230204-163852_9313205f-ffd4-482a-8e4b-90190fe206c2 | 0.79023
21.18 | 32.53 | 5504.63 | 7.6 | [45.44, 76.38] | [24.98, 4.31] | [10.12, 10.12] | [4.87, 15.14] | 0 | 917.37 | 80.54 | 90.81 | -10.27 | 7.36 | 88.47 | 67 | 22.7 | 11.35 | 18.39 | 2.79 | 6 | 3522.96 | 1043.55 | 1196.21 | 736.57 | 5.32 | 1.58 | 4.44 | 80.29 | 490 | 4700 | 81.64 | 0.47 | 16.33 | 22.44 | 60 | 9 | 9 | 1.01 | 294 | 303.08 | 404568.87 | 282408.46 | 20230204-163852_1304ddfc-af5f-4c90-81db-1d63ad22f719 | 6.9726
21.84 | 32.68 | 5487.67 | 7.6 | [31.86, 51.39] | [15.08, 3.72] | [11.1, 11.1] | [2.01, 10.19] | 0 | 911.87 | 58.04 | 66.21 | -8.17 | 7.45 | 89.74 | 70 | 21.7 | 10.84 | 17.86 | 3.97 | 6.02 | 3512.11 | 1047.79 | 1247.28 | 751.73 | 5.7 | 1.61 | 4.37 | 73.18 | 490 | 4700 | 77.98 | 0.47 | 15.54 | 33.34 | 60 | 9 | 9 | 0.68 | 294 | 300.11 | 242922.77 | 203858.12 | 20230204-163852_ad8b0826-c7db-4aa8-9ca0-ed0a3d544bb5 | 2.2297
21.67 | 32.18 | 5525.93 | 7.6 | [7.54, 23.27] | [14.93, 1.46] | [7.55, 7.55] | [2.35, 4.61] | 0 | 479.63 | 30.02 | 32.28 | -2.26 | 7.1 | 90.62 | 71 | 21.7 | 10.51 | 17.99 | 3.67 | 11.52 | 3536.6 | 1079.57 | 1523.36 | 823.61 | 6.51 | 1.71 | 4.18 | 74.11 | 490 | 4700 | 75.6 | 0.47 | 7.19 | 73.64 | 60 | 9 | 9 | 0.31 | 294 | 296.77 | 220301.08 | 91798.94 | 20230204-163852_84c1a374-b60c-4693-b453-c83eb51da72b | 7.3346
21.95 | 32.57 | 5450.82 | 7.59 | [17.83, 38.21] | [14.97, 0.17] | [10.8, 10.8] | [2.0, 7.57] | 0 | 716.08 | 43.6 | 49.18 | -5.58 | 7.33 | 89.84 | 69 | 22 | 10.62 | 18.01 | 3.93 | 7.61 | 3488.52 | 1052.26 | 1349.34 | 776.37 | 5.76 | 1.64 | 4.31 | 72.97 | 490 | 4700 | 76.39 | 0.47 | 11.55 | 44.89 | 60 | 9 | 9 | 0.5 | 294 | 298.54 | 229031.37 | 121859.75 | 20230204-163852_1fd1339f-62ab-4dcb-8781-3a8d1dbcf50a | 6.1171
22.12 | 32.98 | 5436.66 | 7.62 | [69.86, 89.27] | [14.99, 5.14] | [11.73, 11.73] | [8.13, 17.69] | 0 | 1155.87 | 96.58 | 106.14 | -9.56 | 7.59 | 89.75 | 75 | 21.7 | 10.86 | 18.52 | 3.61 | 4.7 | 3479.46 | 1029.24 | 1151.01 | 721.99 | 5.46 | 1.59 | 4.43 | 75.07 | 490 | 4700 | 78.11 | 0.47 | 21.09 | 19.2 | 60 | 9 | 9 | 1.18 | 294 | 304.61 | 337881.73 | 331304.21 | 20230204-163852_78835765-2c43-408f-bd6e-32bdbc233ece | 0.37543
21.5 | 31.86 | 5584.06 | 7.59 | [70.22, 70.22] | [17.77, 17.77] | [6.46, 6.46] | [8.56, 8.56] | 0 | 1172 | 94.45 | 94.45 | 0 | 7.53 | 88.78 | 71 | 21.6 | 10.36 | 17.9 | 3.6 | 4.76 | 3573.8 | 1052.34 | 1146.22 | 730.26 | 11.03 | 1.57 | 4.46 | 74.24 | 490 | 4700 | 74.52 | 0.47 | 19.79 | 39.66 | 60 | 9 | 9 | 0.57 | 294 | 299.14 | 372109.11 | 372109.11 | 20230204-163852_57893447-e073-4651-a9f3-1eb7a23f4001 | 0
21.19 | 32.48 | 5529.53 | 7.59 | [6.74, 36.0] | [24.99, 0.23] | [10.11, 10.11] | [2.63, 7.13] | 0 | 341.63 | 41.84 | 46.34 | -4.5 | 6.95 | 88.23 | 69 | 22.4 | 11.29 | 18.38 | 2.81 | 16.19 | 3538.9 | 1092.31 | 1688.14 | 860.39 | 5.87 | 1.74 | 4.11 | 80.1 | 490 | 4700 | 81.19 | 0.47 | 5.35 | 47.64 | 60 | 9 | 9 | 0.48 | 294 | 298.28 | 347975.21 | 115631.39 | 20230204-163852_872877e1-d342-4fbe-9992-136e0723f9d9 | 13.2616
21.47 | 31.67 | 5545.71 | 7.62 | [70.15, 70.15] | [20.04, 20.04] | [6.41, 6.41] | [10.0, 10.0] | 0 | 1145.49 | 96.6 | 96.6 | 0 | 7.5 | 89.73 | 68 | 22 | 10.2 | 17.88 | 3.59 | 4.84 | 3549.25 | 1044.9 | 1138.58 | 724.94 | 9.66 | 1.58 | 4.45 | 73.98 | 490 | 4700 | 73.37 | 0.47 | 19.1 | 33.94 | 60 | 9 | 9 | 0.67 | 294 | 300 | 414530.93 | 414530.93 | 20230204-163852_27fbb9ed-067a-4ce1-a42b-25e407e39ad5 | 0
22.04 | 32.73 | 5388.95 | 7.62 | [65.3, 65.3] | [15.02, 15.02] | [11.21, 11.21] | [4.74, 4.74] | 0 | 1141.17 | 91.53 | 91.53 | 0 | 7.58 | 90.29 | 67 | 22.3 | 10.69 | 18.02 | 4.02 | 4.72 | 3448.93 | 1020.34 | 1142.89 | 716.08 | 19.32 | 1.59 | 4.45 | 72.66 | 490 | 4700 | 76.85 | 0.47 | 20.64 | 71.67 | 60 | 9 | 9 | 0.32 | 294 | 296.84 | 299400.68 | 299400.68 | 20230204-163852_e594e12f-a023-458f-933c-e78567b3faaf | 0
21.43 | 32.76 | 5537.98 | 7.6 | [25.31, 56.8] | [25.06, 0.72] | [9.97, 9.97] | [4.1, 11.25] | 0 | 710.04 | 60.34 | 67.49 | -7.15 | 7.21 | 88.06 | 70 | 22.5 | 11.34 | 18.61 | 2.82 | 7.8 | 3544.31 | 1057.2 | 1285.57 | 761.2 | 5.36 | 1.62 | 4.36 | 80.09 | 490 | 4700 | 81.52 | 0.47 | 11.99 | 30.19 | 60 | 9 | 9 | 0.75 | 294 | 300.75 | 379955.79 | 181592.81 | 20230204-163852_614230fe-fc29-4f43-b2ec-be9f90d430a5 | 11.3221
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.58 | 31.73 | 5601.2 | 7.6 | [14.94, 31.0] | [15.03, 0.34] | [5.49, 5.49] | [4.76, 6.14] | 0 | 710.06 | 35.46 | 36.83 | -1.37 | 7.2 | 88.76 | 71 | 21.8 | 10.15 | 18.09 | 3.49 | 7.89 | 3584.77 | 1067.73 | 1289.04 | 766.3 | 5.78 | 1.63 | 4.34 | 74.41 | 490 | 4700 | 73.01 | 0.47 | 10.6 | 55.32 | 60 | 9 | 9 | 0.41 | 294 | 297.68 | 250586.21 | 98544.43 | 20230204-163852_6b79eb15-c747-46dd-b538-1f564e6d7aab | 8.6782
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.41 | 32.37 | 5463.11 | 7.62 | [46.56, 77.89] | [25.02, 4.81] | [9.91, 9.91] | [4.32, 15.44] | 0 | 927.11 | 81.49 | 92.61 | -11.12 | 7.36 | 89.36 | 70 | 22.5 | 10.96 | 18.61 | 2.8 | 5.89 | 3496.39 | 1035.18 | 1182.49 | 729.73 | 5.28 | 1.6 | 4.42 | 79.66 | 490 | 4700 | 78.85 | 0.47 | 16.12 | 22 | 60 | 9 | 9 | 1.03 | 294 | 303.26 | 400189.17 | 292801.2 | 20230204-163852_21dfcd71-d61f-4eac-9b8e-58136c6f9045 | 6.1295
21.91 | 33.65 | 5579.16 | 7.59 | [41.83, 61.27] | [14.93, 0.43] | [11.1, 11.1] | [7.19, 12.13] | 0 | 1006.11 | 67.86 | 72.8 | -4.94 | 7.5 | 87.65 | 80 | 21.1 | 11.73 | 18.59 | 3.33 | 5.55 | 3570.66 | 1061.17 | 1228.98 | 753.73 | 5.59 | 1.61 | 4.38 | 77.9 | 490 | 4700 | 84.38 | 0.47 | 18.56 | 27.99 | 60 | 9 | 9 | 0.81 | 294 | 301.28 | 302479.9 | 191940.54 | 20230204-163852_683d379c-0c81-4f9b-8c14-b13444fa99b3 | 6.3093
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.95 | 32.78 | 5485.93 | 7.6 | [41.12, 65.62] | [14.92, 1.42] | [10.94, 10.94] | [2.0, 13.0] | 0 | 1002.14 | 66.98 | 77.98 | -11 | 7.5 | 89.62 | 73 | 21.5 | 10.84 | 18.07 | 3.88 | 5.47 | 3511 | 1043.45 | 1208.91 | 741.21 | 5.15 | 1.6 | 4.41 | 73.64 | 490 | 4700 | 77.93 | 0.47 | 17.42 | 26.13 | 60 | 9 | 9 | 0.87 | 294 | 301.8 | 248939.13 | 216518.58 | 20230204-163852_93e25903-9081-437c-909a-bb62432b2205 | 1.8505
21.94 | 32.53 | 5411.62 | 7.61 | [20.06, 40.7] | [14.97, 0.38] | [11.31, 11.31] | [2.0, 8.06] | 0 | 751.12 | 46.34 | 52.39 | -6.05 | 7.36 | 90.82 | 68 | 22 | 10.59 | 17.88 | 4.06 | 7.2 | 3463.44 | 1043.09 | 1322.2 | 766.43 | 5.75 | 1.65 | 4.31 | 72.3 | 490 | 4700 | 76.15 | 0.47 | 12.27 | 42.13 | 60 | 9 | 9 | 0.54 | 294 | 298.84 | 231438.25 | 132140.29 | 20230204-163852_9ab28186-2862-4a22-956c-3c4522b45ac2 | 5.6677
21.8 | 33.29 | 5532.14 | 7.6 | [69.23, 69.23] | [14.95, 14.95] | [10.95, 10.95] | [9.36, 9.36] | 0 | 1160.77 | 95.13 | 95.13 | 0 | 7.59 | 88.07 | 79 | 21.5 | 11.49 | 18.84 | 2.96 | 4.77 | 3540.57 | 1046.73 | 1166.63 | 733.27 | 10.16 | 1.59 | 4.43 | 79.49 | 490 | 4700 | 82.6 | 0.47 | 21.93 | 36.28 | 60 | 9 | 9 | 0.62 | 294 | 299.62 | 348700.49 | 348700.49 | 20230204-163852_be190a79-6a95-47c8-b05f-e74f9439b3bc | 0
22.04 | 32.78 | 5478.83 | 7.58 | [25.1, 45.17] | [15.01, 1.9] | [11.1, 11.1] | [2.0, 8.95] | 0 | 830.15 | 51.21 | 58.17 | -6.96 | 7.4 | 89.37 | 73 | 21.8 | 10.74 | 18.35 | 3.69 | 6.6 | 3506.45 | 1050.51 | 1286.98 | 761.82 | 5.72 | 1.61 | 4.36 | 74.43 | 490 | 4700 | 77.22 | 0.47 | 13.79 | 37.95 | 60 | 9 | 9 | 0.6 | 294 | 299.37 | 236133.41 | 163494.52 | 20230204-163852_71345143-f3b8-45fa-a817-ff2dc27eaef5 | 4.1461
22 | 33.08 | 5487.14 | 7.62 | [68.27, 68.27] | [15.06, 15.06] | [10.81, 10.81] | [9.67, 9.67] | 0 | 1156.78 | 94.14 | 94.14 | 0 | 7.58 | 89.06 | 76 | 21.8 | 11.08 | 18.74 | 3.26 | 4.74 | 3511.77 | 1038.2 | 1157.35 | 727.31 | 9.73 | 1.6 | 4.42 | 77.26 | 490 | 4700 | 79.65 | 0.47 | 21.28 | 35.1 | 60 | 9 | 9 | 0.64 | 294 | 299.8 | 352314.37 | 352314.37 | 20230204-163852_2c7361aa-55cf-4672-8dbb-35bfdde4aaa8 | 0
22.25 | 33.54 | 5573.45 | 7.56 | [2.39, 15.81] | [15.06, 0.66] | [11.72, 11.72] | [4.11, 3.13] | 0 | 264.8 | 29.17 | 28.19 | 0.98 | 7.11 | 88.51 | 84 | 21.2 | 11.29 | 19.19 | 3.06 | 21.05 | 3567.01 | 1178.86 | 2345.24 | 1057.01 | 9.31 | 1.9 | 3.75 | 78.69 | 490 | 4700 | 81.18 | 0.47 | 4.05 | 108.39 | 60 | 9 | 9 | 0.21 | 294 | 295.88 | 238772.66 | 64038.25 | 20230204-163852_29dfe2b2-e8b3-40a5-bdb4-8bdca9b16afb | 9.9734
20.18 | 29.89 | 5559.13 | 7.58 | [41.48, 47.09] | [14.99, 12.1] | [6.32, 6.32] | [6.64, 9.36] | 0 | 1055.86 | 62.79 | 65.51 | -2.72 | 7.46 | 91.52 | 64 | 19.2 | 9.71 | 14.79 | 5.39 | 5.27 | 3557.84 | 1050.72 | 1172.01 | 735.08 | 6.71 | 1.54 | 4.51 | 64.29 | 490 | 4700 | 69.79 | 0.47 | 16.36 | 36.29 | 60 | 9 | 9 | 0.62 | 294 | 299.61 | 293219.6 | 290216.81 | 20230204-164514_80d71a9e-77a5-407d-8711-3581c0b54066 | 0.17139
20.98 | 30.4 | 5454.57 | 7.61 | [39.7, 59.82] | [15.02, 4.76] | [6.57, 6.57] | [2.0, 11.86] | 0 | 1038.35 | 61.29 | 71.15 | -9.86 | 7.45 | 93.22 | 74 | 18.8 | 9.43 | 15.65 | 5.33 | 5.25 | 3490.92 | 1031.63 | 1156.32 | 722.99 | 5.17 | 1.57 | 4.47 | 63.89 | 490 | 4700 | 67.78 | 0.47 | 15.94 | 28.64 | 60 | 9 | 9 | 0.79 | 294 | 301.11 | 245013.58 | 237019.66 | 20230204-164514_14fce8ee-f0ec-4a1f-8f9b-92d3d9e56dde | 0.45627
21.38 | 31.79 | 5631.7 | 7.58 | [18.33, 41.21] | [19.45, 1.22] | [6.55, 6.55] | [3.51, 8.16] | 0 | 696.38 | 44.33 | 48.98 | -4.65 | 7.17 | 88.41 | 68 | 22 | 10.41 | 17.88 | 3.5 | 8.09 | 3604.29 | 1072.67 | 1292.3 | 768.73 | 5.43 | 1.61 | 4.37 | 74.85 | 490 | 4700 | 74.85 | 0.47 | 10.56 | 41.6 | 60 | 9 | 9 | 0.54 | 294 | 298.9 | 295974.38 | 139773.95 | 20230204-164514_5157bb7f-81bb-4b1c-a388-15bd93914918 | 8.9155
21.73 | 31.65 | 5589.72 | 7.59 | [102.63, 102.63] | [19.97, 19.97] | [6.33, 6.33] | [2.04, 2.04] | 0 | 1245.96 | 128.93 | 128.93 | 0 | 7.58 | 89.33 | 72 | 21.7 | 9.91 | 18.13 | 3.61 | 4.49 | 3577.42 | 1051.84 | 1131.34 | 726.85 | 63.31 | 1.56 | 4.48 | 73.32 | 490 | 4700 | 71.29 | 0.47 | 20.45 | 166.73 | 60 | 9 | 9 | 0.14 | 294 | 295.22 | 361071.45 | 361071.45 | 20230204-164514_fe81d17b-fff4-4284-a53f-54499df1cfb1 | 0
20.51 | 30.02 | 5480.88 | 7.61 | [37.11, 55.88] | [15.02, 4.09] | [6.48, 6.48] | [3.23, 11.08] | 0 | 1017.21 | 58.61 | 66.45 | -7.84 | 7.44 | 93.07 | 67 | 19.6 | 9.51 | 15.53 | 4.97 | 5.39 | 3507.76 | 1037.02 | 1166.67 | 727.62 | 5.29 | 1.56 | 4.48 | 65.68 | 490 | 4700 | 68.41 | 0.47 | 15.59 | 30.66 | 60 | 9 | 9 | 0.74 | 294 | 300.65 | 255240.49 | 217342.53 | 20230204-164514_ecad33ea-fca9-4346-a073-2836924fb682 | 2.1631
20.09 | 29.81 | 5519.65 | 7.6 | [63.27, 63.27] | [15.03, 15.03] | [6.73, 6.73] | [9.81, 9.81] | 0 | 1175.85 | 85.03 | 85.03 | 0 | 7.55 | 91.82 | 56 | 20.2 | 9.72 | 14.67 | 5.42 | 4.69 | 3532.58 | 1041.15 | 1139.66 | 724.03 | 8.66 | 1.54 | 4.53 | 64.18 | 490 | 4700 | 69.86 | 0.47 | 18.91 | 34.6 | 60 | 9 | 9 | 0.65 | 294 | 299.89 | 345331.82 | 345331.82 | 20230204-164514_9582669a-4c03-4f6e-803b-2f54f7ddb94c | 0
20.86 | 30.37 | 5550.1 | 7.6 | [9.3, 25.62] | [14.91, 0.54] | [6.82, 6.82] | [3.13, 5.07] | 0 | 544.25 | 31.03 | 32.98 | -1.95 | 7.12 | 92.08 | 80 | 18.8 | 9.51 | 16.38 | 4.48 | 10.2 | 3552.06 | 1073.79 | 1431.2 | 800.33 | 6.12 | 1.66 | 4.27 | 67.96 | 490 | 4700 | 68.36 | 0.47 | 7.43 | 66.93 | 60 | 9 | 9 | 0.34 | 294 | 297.04 | 228826.63 | 86624.5 | 20230204-164514_51bad202-2151-4da0-b4b0-05344ba1eac0 | 8.1166
21.5 | 30.94 | 5455.99 | 7.62 | [59.84, 59.84] | [16.45, 16.45] | [6.58, 6.58] | [2.03, 2.03] | 0 | 1142.8 | 82.87 | 82.87 | 0 | 7.52 | 93.02 | 81 | 18.8 | 9.44 | 16.5 | 5.01 | 4.77 | 3491.83 | 1029.17 | 1128.88 | 715.96 | 40.88 | 1.58 | 4.47 | 65.35 | 490 | 4700 | 67.88 | 0.47 | 17.99 | 167.53 | 60 | 9 | 9 | 0.14 | 294 | 295.22 | 280473.56 | 280473.56 | 20230204-164514_79317119-6a13-417d-baf4-283685540ca9 | 0
20.44 | 30.04 | 5549.61 | 7.6 | [23.29, 41.08] | [14.96, 0.73] | [7.0, 7.0] | [4.57, 8.14] | 0 | 850.7 | 45.25 | 48.81 | -3.56 | 7.34 | 91.84 | 64 | 19.6 | 9.6 | 15.16 | 5.29 | 6.52 | 3551.75 | 1056.05 | 1242.64 | 752.68 | 5.56 | 1.59 | 4.42 | 64.48 | 490 | 4700 | 69.01 | 0.47 | 12.49 | 41.74 | 60 | 9 | 9 | 0.54 | 294 | 298.88 | 256452.52 | 133774.82 | 20230204-164514_6231f9f2-fdd2-4368-a36a-7fc610eaaee7 | 7.0022
21.82 | 31.38 | 5485.31 | 7.63 | [82.34, 82.34] | [19.73, 19.73] | [6.57, 6.57] | [2.56, 2.56] | 0 | 1191.72 | 108.64 | 108.64 | 0 | 7.54 | 91.73 | 71 | 21.6 | 9.56 | 17.9 | 3.92 | 4.6 | 3510.6 | 1033.06 | 1119.81 | 715.65 | 42.43 | 1.59 | 4.45 | 70.93 | 490 | 4700 | 68.77 | 0.47 | 19.09 | 132.63 | 60 | 9 | 9 | 0.17 | 294 | 295.54 | 345823.77 | 345823.77 | 20230204-164514_84e4b75f-319b-4b47-aee6-f7a81f7ba4a6 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.74 | 31.49 | 5462.6 | 7.61 | [65.38, 65.38] | [20.06, 20.06] | [6.47, 6.47] | [2.0, 2.0] | 0 | 1124.25 | 91.91 | 91.91 | 0 | 7.49 | 90.35 | 70 | 22.2 | 9.75 | 18.33 | 3.41 | 4.86 | 3496.06 | 1029.59 | 1125.54 | 715.05 | 45.91 | 1.57 | 4.47 | 74.1 | 490 | 4700 | 70.1 | 0.47 | 18.17 | 169.62 | 60 | 9 | 9 | 0.13 | 294 | 295.2 | 329261.69 | 329261.69 | 20230204-164514_839e933d-fbbc-4c9f-a003-fc9a71d216bb | 0
21.43 | 31.64 | 5582.41 | 7.58 | [4.49, 24.45] | [19.95, 0.71] | [6.32, 6.32] | [4.12, 4.84] | 0 | 309.25 | 30.76 | 31.48 | -0.72 | 6.87 | 90.01 | 62 | 22.4 | 10.21 | 17.44 | 3.99 | 18.05 | 3572.74 | 1095.71 | 1681.12 | 855.23 | 6.35 | 1.73 | 4.12 | 71.92 | 490 | 4700 | 73.43 | 0.47 | 4.31 | 70.12 | 60 | 9 | 9 | 0.32 | 294 | 296.91 | 295985.25 | 84850.14 | 20230204-164514_28f7cf87-bc8a-4553-80e9-80af668123f9 | 12.0511
20.65 | 30.33 | 5519.42 | 7.58 | [54.42, 79.84] | [14.99, 0.59] | [6.53, 6.53] | [4.78, 15.81] | 0 | 1136.37 | 75.94 | 86.96 | -11.02 | 7.52 | 91.52 | 73 | 18.6 | 9.68 | 15.34 | 5.31 | 4.86 | 3532.43 | 1041.73 | 1146.79 | 725.73 | 4.8 | 1.53 | 4.52 | 64.58 | 490 | 4700 | 69.59 | 0.47 | 18.04 | 21.48 | 60 | 9 | 9 | 1.05 | 294 | 303.49 | 285782.21 | 243526.42 | 20230204-164514_928edafe-f4e8-4d62-828e-81aa9532f232 | 2.4119
22.24 | 31.7 | 5470.51 | 7.6 | [22.23, 47.19] | [20.0, 2.39] | [6.52, 6.52] | [2.0, 9.35] | 0 | 756.64 | 48.75 | 56.1 | -7.35 | 7.21 | 91.37 | 75 | 21.6 | 9.46 | 18.42 | 3.82 | 7.23 | 3501.13 | 1039.27 | 1225.46 | 739.34 | 5.21 | 1.61 | 4.38 | 71.23 | 490 | 4700 | 68.01 | 0.47 | 10.92 | 36.31 | 60 | 9 | 9 | 0.62 | 294 | 299.61 | 290843.5 | 171405.18 | 20230204-164514_1bb62aef-2a50-423f-abf6-443f25699192 | 6.8173
20.11 | 29.76 | 5496.71 | 7.6 | [55.96, 75.88] | [14.99, 0.17] | [6.58, 6.58] | [9.93, 15.03] | 0 | 1143.74 | 77.53 | 82.63 | -5.1 | 7.53 | 92.15 | 62 | 19.8 | 9.65 | 15.09 | 5.03 | 4.81 | 3517.89 | 1037.34 | 1140.84 | 722.45 | 5.16 | 1.53 | 4.53 | 65.74 | 490 | 4700 | 69.37 | 0.47 | 18.23 | 22.6 | 60 | 9 | 9 | 1 | 294 | 303.02 | 339499.87 | 227036.39 | 20230204-164514_29da8392-1714-45f2-ab56-5cbb3678e7bb | 6.4191
20.55 | 30.04 | 5515.69 | 7.61 | [24.9, 43.59] | [15.01, 1.72] | [6.5, 6.5] | [3.23, 8.64] | 0 | 879.52 | 46.41 | 51.81 | -5.4 | 7.34 | 92.41 | 73 | 18.7 | 9.49 | 15.43 | 5.11 | 6.27 | 3530.04 | 1047.58 | 1216.89 | 743.01 | 5.37 | 1.59 | 4.43 | 64.98 | 490 | 4700 | 68.24 | 0.47 | 12.95 | 39.32 | 60 | 9 | 9 | 0.58 | 294 | 299.18 | 244442.31 | 152709.63 | 20230204-164514_ecc3eece-6e90-44e7-8b84-d5beb58184ad | 5.2359
19.76 | 29.84 | 5516 | 7.6 | [41.96, 57.0] | [15.01, 2.99] | [7.78, 7.78] | [8.27, 11.29] | 0 | 1042.19 | 64.75 | 67.77 | -3.02 | 7.48 | 91.91 | 61 | 20 | 10.08 | 15.14 | 4.62 | 5.29 | 3530.24 | 1044.54 | 1178.36 | 734.09 | 5.73 | 1.55 | 4.51 | 68.57 | 490 | 4700 | 72.5 | 0.47 | 16.89 | 30.07 | 60 | 9 | 9 | 0.75 | 294 | 300.78 | 311641.18 | 208156.36 | 20230204-164514_cf1fd2ab-3e79-4f6b-b48d-dd43ca290294 | 5.9067
20.32 | 29.9 | 5471.12 | 7.6 | [49.62, 62.36] | [15.0, 5.37] | [6.44, 6.44] | [9.25, 12.36] | 0 | 1109.96 | 71.06 | 74.17 | -3.11 | 7.5 | 92.26 | 60 | 20.3 | 9.58 | 15.28 | 5.04 | 4.93 | 3501.52 | 1033.06 | 1141.87 | 720.62 | 5.75 | 1.54 | 4.52 | 65.52 | 490 | 4700 | 68.87 | 0.47 | 17.53 | 27.47 | 60 | 9 | 9 | 0.82 | 294 | 301.42 | 327050.17 | 251783.54 | 20230204-164514_03e995f6-be00-47fc-b141-d6c7b0d0853d | 4.296
20.12 | 30.02 | 5478.18 | 7.61 | [38.85, 53.41] | [14.94, 2.76] | [7.33, 7.33] | [8.21, 10.58] | 0 | 1023.41 | 61.12 | 63.5 | -2.38 | 7.46 | 92.17 | 61 | 20.2 | 9.9 | 15.32 | 4.8 | 5.35 | 3506.04 | 1037.42 | 1172.23 | 729.35 | 5.78 | 1.56 | 4.49 | 67.34 | 490 | 4700 | 71.18 | 0.47 | 16.35 | 32.09 | 60 | 9 | 9 | 0.71 | 294 | 300.35 | 307111.95 | 194571.9 | 20230204-164514_2d60ad7c-07a6-48ce-96e6-3ff78d1a2c11 | 6.4235
20.56 | 30.11 | 5500.84 | 7.6 | [67.28, 67.28] | [14.96, 14.96] | [6.6, 6.6] | [4.91, 4.91] | 0 | 1194.5 | 88.84 | 88.84 | 0 | 7.56 | 92.06 | 73 | 19.2 | 9.54 | 15.9 | 4.66 | 4.61 | 3520.54 | 1037.19 | 1131.53 | 720.45 | 18.07 | 1.54 | 4.52 | 67.2 | 490 | 4700 | 68.63 | 0.47 | 19.04 | 69.09 | 60 | 9 | 9 | 0.33 | 294 | 296.95 | 298069.33 | 298069.33 | 20230204-164514_54499e68-c359-44e9-b68f-c5bad4740bc1 | 0
20.6 | 30.07 | 5467.78 | 7.6 | [55.57, 81.99] | [14.97, 0.61] | [6.69, 6.69] | [4.17, 16.24] | 0 | 1140.71 | 77.23 | 89.29 | -12.06 | 7.53 | 92.91 | 74 | 18.4 | 9.47 | 15.27 | 5.32 | 4.79 | 3499.38 | 1032.04 | 1136.21 | 719.05 | 4.76 | 1.54 | 4.52 | 64.01 | 490 | 4700 | 68.1 | 0.47 | 17.95 | 20.91 | 60 | 9 | 9 | 1.08 | 294 | 303.74 | 280583.24 | 250184.4 | 20230204-164514_45475a7f-7574-4140-a1de-b440ed5bd7a0 | 1.7351
20.74 | 30.09 | 5498.27 | 7.61 | [14.0, 33.66] | [15.08, 0.02] | [6.31, 6.31] | [2.05, 6.67] | 0 | 677.65 | 35.39 | 39.99 | -4.6 | 7.2 | 92.61 | 82 | 18.4 | 9.35 | 16.23 | 4.51 | 8.11 | 3518.89 | 1052.2 | 1301.16 | 762.4 | 5.31 | 1.62 | 4.37 | 67.45 | 490 | 4700 | 67.23 | 0.47 | 9.45 | 50.94 | 60 | 9 | 9 | 0.44 | 294 | 298 | 223499.88 | 103038.52 | 20230204-164514_1ddf0bb0-56b9-41f4-9bda-3dac288c62de | 6.8756
20.1 | 29.89 | 5544.27 | 7.6 | [55.96, 69.79] | [15.0, 6.39] | [6.84, 6.84] | [8.62, 13.84] | 0 | 1140.9 | 77.8 | 83.02 | -5.22 | 7.53 | 91.62 | 62 | 19.6 | 9.79 | 14.9 | 5.2 | 4.86 | 3548.33 | 1046.59 | 1152.88 | 729.36 | 5.62 | 1.54 | 4.51 | 65.32 | 490 | 4700 | 70.38 | 0.47 | 18.24 | 24.54 | 60 | 9 | 9 | 0.92 | 294 | 302.3 | 326498.59 | 286103.27 | 20230204-164514_a5249d55-0fac-457b-9e58-f6215028f2e2 | 2.3057
22.09 | 31.63 | 5449.19 | 7.62 | [52.88, 52.88] | [20.0, 20.0] | [6.34, 6.34] | [2.0, 2.0] | 0 | 1060.89 | 79.22 | 79.22 | 0 | 7.44 | 91.09 | 73 | 22.1 | 9.54 | 18.63 | 3.45 | 5.14 | 3487.48 | 1027.94 | 1133.9 | 715.85 | 39.67 | 1.59 | 4.44 | 73.42 | 490 | 4700 | 68.61 | 0.47 | 16.59 | 170.06 | 60 | 9 | 9 | 0.13 | 294 | 295.2 | 317387.56 | 317387.56 | 20230204-164514_25da6688-3873-4b27-bcba-db7d4f61ebb0 | 0
21.53 | 31.56 | 5505.71 | 7.62 | [69.91, 69.91] | [20.0, 20.0] | [6.5, 6.5] | [4.38, 4.38] | 0 | 1144.17 | 96.41 | 96.41 | 0 | 7.5 | 89.6 | 68 | 22.1 | 10.03 | 17.97 | 3.55 | 4.81 | 3523.65 | 1037.46 | 1131.17 | 719.95 | 22.03 | 1.58 | 4.46 | 73.84 | 490 | 4700 | 72.13 | 0.47 | 18.92 | 77.58 | 60 | 9 | 9 | 0.29 | 294 | 296.63 | 356680.79 | 356680.79 | 20230204-164514_4fe29a84-02e9-4731-8a3f-8b8a9cd627a9 | 0
20.43 | 31.13 | 5535.76 | 7.6 | [45.66, 70.51] | [19.95, 4.34] | [8.99, 8.99] | [4.73, 13.97] | 0 | 988.1 | 74.6 | 83.84 | -9.24 | 7.42 | 91.15 | 52 | 21 | 10.7 | 14.83 | 5.6 | 5.6 | 3542.89 | 1048.54 | 1189.24 | 737.84 | 5.34 | 1.56 | 4.47 | 65.65 | 490 | 4700 | 76.95 | 0.47 | 16.72 | 24.3 | 60 | 9 | 9 | 0.93 | 294 | 302.38 | 340595.45 | 264844.14 | 20230204-165137_c295c30f-170f-446e-93cd-7100bdc267ab | 4.3237
20.81 | 31.01 | 5462.72 | 7.62 | [43.63, 62.24] | [20.0, 9.29] | [8.74, 8.74] | [4.45, 12.35] | 0 | 974.31 | 72.37 | 80.27 | -7.9 | 7.41 | 92.17 | 67 | 19.4 | 10.2 | 15.35 | 5.47 | 5.61 | 3496.14 | 1034.8 | 1175.5 | 728.46 | 5.86 | 1.58 | 4.46 | 65.11 | 490 | 4700 | 73.35 | 0.47 | 15.92 | 27.5 | 60 | 9 | 9 | 0.82 | 294 | 301.41 | 336370.53 | 301547.64 | 20230204-165137_80245d9c-ca9b-4b15-90d8-d1451956c24a | 1.9876
20.6 | 31.13 | 5528.92 | 7.6 | [22.07, 47.86] | [20.1, 0.42] | [8.59, 8.59] | [3.37, 9.48] | 0 | 734.25 | 50.76 | 56.87 | -6.11 | 7.24 | 91.71 | 58 | 20.8 | 10.54 | 15.46 | 5.13 | 7.53 | 3538.51 | 1055.62 | 1280.34 | 759.85 | 5.36 | 1.6 | 4.39 | 67.25 | 490 | 4700 | 75.76 | 0.47 | 11.6 | 35.83 | 60 | 9 | 9 | 0.63 | 294 | 299.69 | 307517.43 | 150863.23 | 20230204-165137_9621d0bf-4c6a-46cc-8757-cb5eb4044f98 | 8.9414
19.8 | 29.91 | 5481.85 | 7.6 | [53.47, 53.47] | [14.96, 14.96] | [7.74, 7.74] | [8.73, 8.73] | 0 | 1118.39 | 76.17 | 76.17 | 0 | 7.53 | 91.77 | 63 | 19.9 | 10.11 | 15.3 | 4.49 | 4.9 | 3508.38 | 1036.09 | 1150.8 | 724.3 | 8.72 | 1.53 | 4.53 | 69.22 | 490 | 4700 | 72.71 | 0.47 | 18.64 | 38.9 | 60 | 9 | 9 | 0.58 | 294 | 299.24 | 325818.9 | 325818.9 | 20230204-165137_1c14ce1a-dfc5-4646-8807-d96978ce9869 | 0
21.01 | 31.13 | 5502.83 | 7.6 | [48.25, 70.39] | [20.03, 4.88] | [8.43, 8.43] | [6.96, 13.95] | 0 | 1010.77 | 76.71 | 83.7 | -6.99 | 7.43 | 91.57 | 65 | 20.1 | 10.12 | 15.74 | 5.27 | 5.44 | 3521.81 | 1041.12 | 1171.53 | 730.48 | 5.5 | 1.57 | 4.46 | 65.76 | 490 | 4700 | 72.79 | 0.47 | 16.38 | 24.34 | 60 | 9 | 9 | 0.93 | 294 | 302.37 | 366029.63 | 270698.69 | 20230204-165137_f89eb99b-363b-4019-9653-0829b3735acf | 5.4413
20.74 | 31.03 | 5498.39 | 7.62 | [73.12, 73.12] | [20.06, 20.06] | [9.42, 9.42] | [6.46, 6.46] | 0 | 1131.95 | 102.6 | 102.6 | 0 | 7.53 | 91.93 | 63 | 20.4 | 10.29 | 15.76 | 4.98 | 4.86 | 3518.97 | 1038.29 | 1146.61 | 724.24 | 15.89 | 1.57 | 4.48 | 67.37 | 490 | 4700 | 73.99 | 0.47 | 19.18 | 52.59 | 60 | 9 | 9 | 0.43 | 294 | 297.87 | 383898.99 | 383898.99 | 20230204-165137_d633fee3-c775-453b-99c0-6054e444eeec | 0
20.88 | 30.7 | 5489.83 | 7.6 | [47.63, 65.59] | [17.42, 4.23] | [8.18, 8.18] | [8.24, 13.0] | 0 | 1043.52 | 73.23 | 78 | -4.77 | 7.47 | 92.19 | 74 | 19 | 9.82 | 15.84 | 5.04 | 5.26 | 3513.49 | 1038.73 | 1166.5 | 728.62 | 5.63 | 1.56 | 4.48 | 66.1 | 490 | 4700 | 70.62 | 0.47 | 16.57 | 26.12 | 60 | 9 | 9 | 0.87 | 294 | 301.8 | 346297.29 | 248540.54 | 20230204-165137_ad972651-7591-4bd0-a4fa-91be4000cca2 | 5.5797
20.47 | 30.29 | 5525.44 | 7.59 | [39.73, 60.76] | [20.03, 5.15] | [6.36, 6.36] | [5.9, 12.05] | 0 | 964.86 | 66.12 | 72.27 | -6.15 | 7.36 | 91.73 | 65 | 19.5 | 9.82 | 15.19 | 5.28 | 5.73 | 3536.28 | 1044.06 | 1170.91 | 730.83 | 5.49 | 1.55 | 4.5 | 65.05 | 490 | 4700 | 70.64 | 0.47 | 14.94 | 28.19 | 60 | 9 | 9 | 0.8 | 294 | 301.23 | 345949.71 | 244358.84 | 20230204-165137_95364b8d-c523-4e87-b884-1cae28969ae8 | 5.7986
20.4 | 30.16 | 5504.54 | 7.6 | [49.76, 76.04] | [19.96, 0.71] | [6.07, 6.07] | [8.03, 15.06] | 0 | 1044.41 | 75.79 | 82.82 | -7.03 | 7.42 | 91.98 | 62 | 20.3 | 9.75 | 15.54 | 4.87 | 5.27 | 3522.91 | 1038.38 | 1146.76 | 723.26 | 5.03 | 1.55 | 4.51 | 66.72 | 490 | 4700 | 70.15 | 0.47 | 16.43 | 22.55 | 60 | 9 | 9 | 1 | 294 | 303.03 | 375240.3 | 233674.17 | 20230204-165137_8604d278-3aad-43ea-bda4-86f580182269 | 8.0803
20.66 | 30.78 | 5492.63 | 7.6 | [37.68, 61.26] | [19.95, 3.39] | [8.19, 8.19] | [5.12, 12.14] | 0 | 929.58 | 65.82 | 72.84 | -7.02 | 7.37 | 92.44 | 61 | 20.4 | 10.12 | 15.5 | 5.17 | 5.91 | 3515.28 | 1041.06 | 1190.76 | 734.33 | 5.42 | 1.57 | 4.46 | 66.2 | 490 | 4700 | 72.76 | 0.47 | 14.82 | 27.97 | 60 | 9 | 9 | 0.81 | 294 | 301.28 | 336925.1 | 225747.4 | 20230204-165137_61379513-1a10-45da-a506-17b1d58992b0 | 6.3458
20.75 | 30.95 | 5474.61 | 7.62 | [48.74, 71.97] | [20.01, 5.33] | [8.29, 8.29] | [5.72, 14.27] | 0 | 1015.7 | 77.04 | 85.59 | -8.55 | 7.43 | 92.52 | 60 | 20.4 | 10.21 | 15.37 | 5.38 | 5.39 | 3503.75 | 1035.54 | 1163.31 | 726.12 | 5.4 | 1.58 | 4.47 | 65.5 | 490 | 4700 | 73.4 | 0.47 | 16.72 | 23.8 | 60 | 9 | 9 | 0.95 | 294 | 302.56 | 353420.66 | 280593.83 | 20230204-165137_1ad3bebf-ae09-44ab-ae51-d0dd3b712525 | 4.1568
21.13 | 31.2 | 5454.5 | 7.59 | [57.54, 57.54] | [20.03, 20.03] | [9.0, 9.0] | [6.25, 6.25] | 0 | 1062.88 | 86.57 | 86.57 | 0 | 7.47 | 92.09 | 63 | 20.3 | 10.07 | 15.67 | 5.46 | 5.13 | 3490.88 | 1031.25 | 1151.62 | 721.9 | 13.84 | 1.55 | 4.49 | 64.85 | 490 | 4700 | 72.42 | 0.47 | 17.53 | 54.3 | 60 | 9 | 9 | 0.42 | 294 | 297.75 | 367485.32 | 367485.32 | 20230204-165137_ed6c7eee-d2e2-4d7a-93ee-5165566a2390 | 0
20.82 | 31.03 | 5460.81 | 7.59 | [46.02, 46.02] | [20.01, 20.01] | [9.15, 9.15] | [3.11, 3.11] | 0 | 988.52 | 75.18 | 75.18 | 0 | 7.43 | 92.08 | 61 | 20.6 | 10.21 | 15.68 | 5.14 | 5.52 | 3494.92 | 1034.46 | 1173.96 | 728.12 | 24.17 | 1.55 | 4.49 | 66.5 | 490 | 4700 | 73.4 | 0.47 | 16.22 | 109.18 | 60 | 9 | 9 | 0.21 | 294 | 295.87 | 325358.44 | 325358.44 | 20230204-165137_b3c632c6-212c-4083-9a0a-b35a3a3f3f9d | 0
19.98 | 29.96 | 5512.16 | 7.59 | [44.94, 59.01] | [15.08, 3.87] | [7.29, 7.29] | [8.84, 11.69] | 0 | 1068.51 | 67.31 | 70.17 | -2.86 | 7.49 | 91.86 | 67 | 19.4 | 9.98 | 15.35 | 4.63 | 5.16 | 3527.78 | 1042.56 | 1166.35 | 730.45 | 5.76 | 1.54 | 4.52 | 68.3 | 490 | 4700 | 71.75 | 0.47 | 17.25 | 29.04 | 60 | 9 | 9 | 0.78 | 294 | 301.02 | 320579.34 | 224342.34 | 20230204-165137_cff838f3-6e5d-4516-81e5-19207da7ac79 | 5.493
20.92 | 31.07 | 5453.25 | 7.6 | [34.5, 61.54] | [20.02, 3.13] | [8.49, 8.49] | [2.04, 12.19] | 0 | 894.83 | 63.01 | 73.16 | -10.15 | 7.35 | 92.35 | 68 | 19.5 | 10.14 | 15.57 | 5.36 | 6.09 | 3490.08 | 1034.98 | 1195.98 | 732.68 | 5.17 | 1.57 | 4.46 | 65.43 | 490 | 4700 | 72.93 | 0.47 | 14.32 | 27.85 | 60 | 9 | 9 | 0.81 | 294 | 301.32 | 303890.24 | 223681.52 | 20230204-165137_348859cd-0c7c-4d38-8271-ee07aa4de376 | 4.5781
20.42 | 30.69 | 5494.1 | 7.6 | [34.3, 57.57] | [20.02, 1.28] | [9.57, 9.57] | [6.88, 11.4] | 0 | 882.6 | 63.89 | 68.42 | -4.53 | 7.36 | 92.08 | 73 | 19.2 | 10.28 | 15.9 | 4.51 | 6.22 | 3516.22 | 1044.58 | 1219.76 | 742.62 | 5.6 | 1.57 | 4.46 | 69.49 | 490 | 4700 | 73.9 | 0.47 | 14.14 | 29.78 | 60 | 9 | 9 | 0.76 | 294 | 300.84 | 353882.45 | 190339.92 | 20230204-165137_aa322059-dd48-4ba5-b2f9-185ff55262df | 9.3346
20.75 | 30.95 | 5501.13 | 7.6 | [24.48, 52.1] | [19.97, 0.64] | [9.17, 9.17] | [2.02, 10.32] | 0 | 767.38 | 53.62 | 61.91 | -8.29 | 7.28 | 92.26 | 65 | 19.8 | 10.2 | 15.47 | 5.29 | 7.17 | 3520.72 | 1050.01 | 1266.38 | 754.75 | 5.2 | 1.6 | 4.4 | 65.87 | 490 | 4700 | 73.35 | 0.47 | 11.89 | 32.91 | 60 | 9 | 9 | 0.69 | 294 | 300.19 | 294936.66 | 166378.19 | 20230204-165137_1f05bf9e-1871-439a-bc77-80884210212d | 7.3378
20.55 | 30.22 | 5515.04 | 7.6 | [46.45, 73.34] | [20.05, 0.36] | [6.17, 6.17] | [7.33, 14.52] | 0 | 1019.43 | 72.67 | 79.87 | -7.2 | 7.4 | 91.97 | 66 | 19.6 | 9.67 | 15.41 | 5.14 | 5.41 | 3529.63 | 1040.86 | 1154.71 | 726.04 | 5 | 1.56 | 4.49 | 65.29 | 490 | 4700 | 69.56 | 0.47 | 15.77 | 23.38 | 60 | 9 | 9 | 0.97 | 294 | 302.71 | 366499.08 | 221619.64 | 20230204-165137_cbcf051a-c141-4f24-afb4-f24ce0d0a08b | 8.2694
21.05 | 31.08 | 5499.34 | 7.59 | [36.4, 58.36] | [19.95, 2.72] | [8.29, 8.29] | [6.83, 11.56] | 0 | 916.43 | 64.64 | 69.37 | -4.73 | 7.36 | 91.85 | 73 | 18.8 | 10.03 | 15.53 | 5.53 | 6 | 3519.58 | 1042.85 | 1197.35 | 736.57 | 5.59 | 1.57 | 4.45 | 64.47 | 490 | 4700 | 72.1 | 0.47 | 14.42 | 29.37 | 60 | 9 | 9 | 0.77 | 294 | 300.94 | 353160.46 | 209295.55 | 20230204-165137_47ea079d-c421-401e-a746-50893cfefd28 | 8.2115
20.39 | 30.8 | 5475.36 | 7.6 | [38.41, 60.69] | [19.97, 2.25] | [9.2, 9.2] | [7.47, 12.02] | 0 | 926.5 | 67.58 | 72.14 | -4.56 | 7.38 | 92.19 | 62 | 20.1 | 10.41 | 15.36 | 5.03 | 5.91 | 3504.23 | 1039.11 | 1196.96 | 735.14 | 5.62 | 1.56 | 4.47 | 67.41 | 490 | 4700 | 74.87 | 0.47 | 15.25 | 28.25 | 60 | 9 | 9 | 0.8 | 294 | 301.21 | 362543.02 | 210940.06 | 20230204-165137_600053d1-8ec0-4598-8a05-325750e6c84b | 8.6531
20.49 | 30.2 | 5520.57 | 7.6 | [46.57, 74.4] | [19.98, 0.15] | [6.48, 6.48] | [6.73, 14.73] | 0 | 1018.2 | 73.03 | 81.03 | -8 | 7.41 | 91.83 | 64 | 19.8 | 9.72 | 15.34 | 5.15 | 5.42 | 3533.16 | 1042.29 | 1158.77 | 727.67 | 4.96 | 1.55 | 4.5 | 65.36 | 490 | 4700 | 69.87 | 0.47 | 15.8 | 23.05 | 60 | 9 | 9 | 0.98 | 294 | 302.84 | 359954.4 | 222337.29 | 20230204-165137_51dfde6a-b18d-4e17-b0ae-86defcc16b18 | 7.8549
20.65 | 31.02 | 5517.52 | 7.59 | [20.86, 47.67] | [19.96, 0.09] | [8.88, 8.88] | [2.5, 9.44] | 0 | 714.06 | 49.7 | 56.64 | -6.94 | 7.23 | 92.28 | 57 | 20.3 | 10.37 | 14.89 | 5.76 | 7.73 | 3531.21 | 1055.16 | 1293.71 | 762.67 | 5.27 | 1.59 | 4.4 | 64.27 | 490 | 4700 | 74.56 | 0.47 | 11.08 | 35.98 | 60 | 9 | 9 | 0.63 | 294 | 299.66 | 296268.06 | 146505.73 | 20230204-165137_64528c0b-c434-498c-ba96-3fe28a466488 | 8.5481
20.33 | 30.9 | 5527.46 | 7.6 | [63.92, 87.62] | [19.99, 7.71] | [8.89, 8.89] | [5.94, 17.37] | 0 | 1096.96 | 92.8 | 104.22 | -11.42 | 7.5 | 91.46 | 55 | 20.9 | 10.57 | 15.15 | 5.18 | 5.04 | 3537.57 | 1044.2 | 1158.27 | 729.32 | 5.34 | 1.55 | 4.5 | 67.11 | 490 | 4700 | 76.01 | 0.47 | 18.82 | 19.55 | 60 | 9 | 9 | 1.16 | 294 | 304.42 | 369346.73 | 355615.02 | 20230204-165137_e48cf637-8546-40cf-8686-cc24dc108b34 | 0.78377
20.34 | 30.13 | 5507.82 | 7.61 | [45.12, 64.3] | [19.99, 5.79] | [6.4, 6.4] | [7.77, 12.75] | 0 | 1008.35 | 71.51 | 76.49 | -4.98 | 7.4 | 92.03 | 63 | 19.8 | 9.78 | 15.21 | 5.13 | 5.46 | 3525 | 1039.97 | 1157.59 | 726.29 | 5.61 | 1.56 | 4.5 | 65.59 | 490 | 4700 | 70.35 | 0.47 | 15.77 | 26.64 | 60 | 9 | 9 | 0.85 | 294 | 301.65 | 369219.09 | 262445 | 20230204-165137_6103b2d8-87eb-43a1-861e-f31ce45dd85e | 6.0944
20.6 | 30.6 | 5509.45 | 7.59 | [34.24, 56.77] | [20.06, 3.6] | [7.13, 7.13] | [5.19, 11.25] | 0 | 904.56 | 61.43 | 67.5 | -6.07 | 7.33 | 92.2 | 60 | 20.1 | 10 | 15.1 | 5.5 | 6.09 | 3526.05 | 1043.44 | 1191.21 | 734.98 | 5.46 | 1.55 | 4.48 | 64.49 | 490 | 4700 | 71.88 | 0.47 | 14.12 | 30.18 | 60 | 9 | 9 | 0.75 | 294 | 300.75 | 335027.26 | 214464.65 | 20230204-165137_ce5974f5-1ab8-43a8-9cf0-58cb35b8613a | 6.8814
20.31 | 30.1 | 5503.49 | 7.6 | [47.68, 62.79] | [14.97, 4.16] | [7.72, 7.72] | [8.15, 12.44] | 0 | 1083.76 | 70.37 | 74.67 | -4.3 | 7.5 | 92.11 | 72 | 18.8 | 9.79 | 15.41 | 4.9 | 5.08 | 3522.23 | 1041.02 | 1163.99 | 729.39 | 5.65 | 1.55 | 4.5 | 66.65 | 490 | 4700 | 70.42 | 0.47 | 17.27 | 27.29 | 60 | 9 | 9 | 0.83 | 294 | 301.47 | 314988.67 | 239186.04 | 20230204-165137_701f1cfc-208c-4cf1-bce0-1049c6a0ea13 | 4.3266
20.52 | 30.14 | 5502.25 | 7.61 | [48.69, 75.61] | [19.98, 1.19] | [5.56, 5.56] | [6.85, 14.97] | 0 | 1041.99 | 74.23 | 82.36 | -8.13 | 7.41 | 92.06 | 64 | 20.5 | 9.62 | 15.98 | 4.55 | 5.28 | 3521.44 | 1037.44 | 1142.76 | 721.79 | 4.96 | 1.56 | 4.5 | 67.91 | 490 | 4700 | 69.17 | 0.47 | 16.16 | 22.68 | 60 | 9 | 9 | 1 | 294 | 302.98 | 362201.64 | 237857.54 | 20230204-165802_af3c21dd-bf35-48d1-8638-df86aa5dfe04 | 7.0973
20.57 | 30.21 | 5528.63 | 7.61 | [38.28, 57.05] | [20.01, 4.69] | [6.11, 6.11] | [7.85, 11.31] | 0 | 954.74 | 64.4 | 67.85 | -3.45 | 7.35 | 92.02 | 66 | 20.1 | 9.64 | 15.87 | 4.7 | 5.79 | 3538.32 | 1044.55 | 1171.73 | 731.09 | 5.69 | 1.57 | 4.47 | 67.23 | 490 | 4700 | 69.32 | 0.47 | 14.47 | 30.02 | 60 | 9 | 9 | 0.75 | 294 | 300.79 | 364047.28 | 227804.86 | 20230204-165802_882cfc9b-5391-4bb1-9670-8bf01bddd76b | 7.7764
20.39 | 30.07 | 5499.68 | 7.59 | [42.33, 68.74] | [20.02, 0.35] | [5.77, 5.77] | [6.87, 13.61] | 0 | 992.68 | 68.12 | 74.86 | -6.74 | 7.38 | 91.72 | 61 | 20.5 | 9.68 | 15.59 | 4.8 | 5.54 | 3519.8 | 1037.96 | 1153.83 | 724.26 | 5 | 1.53 | 4.52 | 66.85 | 490 | 4700 | 69.59 | 0.47 | 15.33 | 24.95 | 60 | 9 | 9 | 0.91 | 294 | 302.17 | 357427.38 | 207881.83 | 20230204-165802_1a0064e4-d9c3-491e-a096-ef05933c299f | 8.5357
20.98 | 30.56 | 5609.03 | 7.61 | [61.16, 86.54] | [20.08, 1.82] | [5.91, 5.91] | [10.02, 17.14] | 0 | 1109.15 | 87.15 | 94.27 | -7.12 | 7.47 | 91.91 | 70 | 20.3 | 9.58 | 16.56 | 4.42 | 5.06 | 3589.78 | 1056.93 | 1154.96 | 733.74 | 5.08 | 1.58 | 4.46 | 68.42 | 490 | 4700 | 68.88 | 0.47 | 16.98 | 19.81 | 60 | 9 | 9 | 1.14 | 294 | 304.28 | 406800.53 | 277435.55 | 20230204-165802_2d2cd15a-700d-48b2-af08-4b6af76811f8 | 7.3838
21.18 | 30.67 | 5602.1 | 7.61 | [46.57, 69.88] | [19.92, 0.45] | [5.78, 5.78] | [9.99, 13.84] | 0 | 1026 | 72.27 | 76.11 | -3.84 | 7.4 | 92.34 | 73 | 20.1 | 9.49 | 16.75 | 4.43 | 5.46 | 3585.34 | 1056.78 | 1168.59 | 736.23 | 5.22 | 1.58 | 4.44 | 68.18 | 490 | 4700 | 68.22 | 0.47 | 15.3 | 24.54 | 60 | 9 | 9 | 0.92 | 294 | 302.3 | 391711.42 | 212396.78 | 20230204-165802_632d1e26-5042-464a-8260-eedaac13669f | 10.2349
20.3 | 29.89 | 5478.13 | 7.61 | [50.2, 77.05] | [20.03, 1.14] | [5.73, 5.73] | [7.3, 15.26] | 0 | 1049.47 | 75.96 | 83.92 | -7.96 | 7.42 | 92.25 | 61 | 20.4 | 9.59 | 15.5 | 4.8 | 5.22 | 3506 | 1032.95 | 1137.6 | 718.71 | 4.98 | 1.55 | 4.52 | 66.64 | 490 | 4700 | 68.99 | 0.47 | 16.35 | 22.25 | 60 | 9 | 9 | 1.02 | 294 | 303.16 | 368888.28 | 241553.85 | 20230204-165802_4afa75e7-47bc-470d-8b86-0bc9a5050d57 | 7.2679
21.04 | 30.52 | 5612.09 | 7.62 | [41.05, 69.52] | [25.03, 0.3] | [5.89, 5.89] | [10.01, 13.77] | 0 | 915.15 | 71.97 | 75.71 | -3.74 | 7.29 | 92.72 | 79 | 19.4 | 9.47 | 16.83 | 4.21 | 6.13 | 3591.74 | 1058.88 | 1183.12 | 739.22 | 5.23 | 1.59 | 4.43 | 69.21 | 490 | 4700 | 68.11 | 0.47 | 13.27 | 24.67 | 60 | 9 | 9 | 0.92 | 294 | 302.26 | 449746.96 | 209682.51 | 20230204-165802_20f46fb5-c188-4943-95dc-6439ebb32ff6 | 13.7023
21.04 | 30.73 | 5655.55 | 7.59 | [24.43, 45.96] | [24.97, 2.55] | [6.14, 6.14] | [9.99, 9.11] | 0 | 726.37 | 55.54 | 54.65 | 0.89 | 7.15 | 91.85 | 71 | 21 | 9.69 | 17.34 | 3.7 | 7.79 | 3619.55 | 1071.34 | 1249.54 | 757.69 | 6.1 | 1.6 | 4.39 | 72.34 | 490 | 4700 | 69.67 | 0.47 | 10.27 | 37.28 | 60 | 9 | 9 | 0.61 | 294 | 299.46 | 434538.26 | 169441.51 | 20230204-165802_1e69a806-01af-404d-8d27-3dcb8095113f | 15.1311
20.67 | 30.28 | 5510.71 | 7.6 | [47.95, 74.87] | [20.06, 0.75] | [5.92, 5.92] | [7.21, 14.83] | 0 | 1032.38 | 73.93 | 81.54 | -7.61 | 7.41 | 92.04 | 67 | 20.1 | 9.6 | 15.99 | 4.68 | 5.34 | 3526.85 | 1039.55 | 1149.12 | 724.2 | 4.99 | 1.55 | 4.49 | 67.24 | 490 | 4700 | 69.05 | 0.47 | 15.92 | 22.9 | 60 | 9 | 9 | 0.99 | 294 | 302.9 | 366485.63 | 230653.25 | 20230204-165802_cb700177-30e7-4a4a-a460-a92cdad547b6 | 7.753
20.98 | 30.64 | 5629.43 | 7.59 | [41.23, 57.37] | [19.94, 5.16] | [5.71, 5.71] | [10.02, 11.37] | 0 | 985.39 | 66.88 | 68.24 | -1.36 | 7.37 | 91.73 | 78 | 19.1 | 9.66 | 16.42 | 4.56 | 5.71 | 3602.84 | 1062.51 | 1182.24 | 741.58 | 5.88 | 1.56 | 4.46 | 67.92 | 490 | 4700 | 69.43 | 0.47 | 14.73 | 29.85 | 60 | 9 | 9 | 0.76 | 294 | 300.82 | 387493.77 | 234162.05 | 20230204-165802_f84c5deb-0886-43dd-a481-fa2d80c75aca | 8.7518
20.88 | 30.49 | 5624.17 | 7.6 | [55.34, 79.18] | [19.95, 1.78] | [5.3, 5.3] | [10.01, 15.68] | 0 | 1085.92 | 80.59 | 86.26 | -5.67 | 7.44 | 91.73 | 74 | 19.7 | 9.62 | 16.5 | 4.38 | 5.18 | 3599.47 | 1059.55 | 1158.17 | 735.37 | 5.14 | 1.56 | 4.47 | 68.71 | 490 | 4700 | 69.15 | 0.47 | 16.55 | 21.65 | 60 | 9 | 9 | 1.05 | 294 | 303.41 | 399497.25 | 255178.89 | 20230204-165802_68e7c892-cc79-4328-8501-4e2634f2ca75 | 8.2373
20.32 | 30.02 | 5492.02 | 7.6 | [53.77, 80.18] | [19.98, 1.47] | [5.69, 5.69] | [7.98, 15.88] | 0 | 1072.67 | 79.44 | 87.34 | -7.9 | 7.44 | 91.82 | 58 | 20.4 | 9.7 | 15.11 | 5.21 | 5.12 | 3514.89 | 1035.21 | 1135.97 | 719.48 | 5 | 1.54 | 4.52 | 65.04 | 490 | 4700 | 69.74 | 0.47 | 16.93 | 21.38 | 60 | 9 | 9 | 1.06 | 294 | 303.53 | 378206.29 | 254642.71 | 20230204-165802_3d66bad6-2018-4905-9424-37488e30796c | 7.0527
20.7 | 30.39 | 5627.57 | 7.61 | [65.51, 96.36] | [24.71, 2.94] | [5.68, 5.68] | [10.01, 19.09] | 0 | 1078.72 | 95.9 | 104.98 | -9.08 | 7.43 | 91.78 | 81 | 19.8 | 9.69 | 17.46 | 3.24 | 5.22 | 3601.64 | 1059.55 | 1154.75 | 734.37 | 5.02 | 1.57 | 4.47 | 74.93 | 490 | 4700 | 69.68 | 0.47 | 16.52 | 17.79 | 60 | 9 | 9 | 1.27 | 294 | 305.45 | 467123.5 | 319398.25 | 20230204-165802_feb252c6-3db4-4791-9927-619e2f709f0e | 8.4318
21.01 | 30.59 | 5639.17 | 7.61 | [23.37, 44.67] | [25.0, 2.55] | [5.89, 5.89] | [10.0, 8.85] | 0 | 711.98 | 54.26 | 53.11 | 1.15 | 7.13 | 92.64 | 80 | 20 | 9.58 | 17.53 | 3.48 | 7.92 | 3609.07 | 1068.04 | 1247.05 | 755.31 | 6.13 | 1.61 | 4.38 | 73.37 | 490 | 4700 | 68.89 | 0.47 | 9.95 | 38.36 | 60 | 9 | 9 | 0.59 | 294 | 299.31 | 433803.33 | 165540.65 | 20230204-165802_70d42718-9c30-4d4f-ad14-5027e8a36bf3 | 15.3118
20.9 | 30.41 | 5551.61 | 7.59 | [40.88, 69.16] | [20.05, 0.79] | [5.38, 5.38] | [4.67, 13.7] | 0 | 984.39 | 66.31 | 75.33 | -9.02 | 7.36 | 92.45 | 77 | 19.6 | 9.51 | 16.78 | 4.12 | 5.64 | 3553.03 | 1047.38 | 1162.75 | 730.3 | 4.84 | 1.56 | 4.48 | 69.76 | 490 | 4700 | 68.37 | 0.47 | 14.74 | 24.79 | 60 | 9 | 9 | 0.91 | 294 | 302.22 | 333864.75 | 214114.6 | 20230204-165802_4f0cadb0-e4dd-469a-98ec-db4abdf80a2a | 6.8351
20.87 | 30.5 | 5544.93 | 7.6 | [44.83, 68.14] | [20.0, 0.2] | [5.87, 5.87] | [9.99, 13.49] | 0 | 1011.26 | 70.7 | 74.21 | -3.51 | 7.39 | 92.04 | 68 | 20.2 | 9.62 | 16.21 | 4.66 | 5.48 | 3548.76 | 1046.31 | 1160.28 | 729.6 | 5.24 | 1.57 | 4.47 | 67.38 | 490 | 4700 | 69.21 | 0.47 | 15.44 | 25.17 | 60 | 9 | 9 | 0.9 | 294 | 302.09 | 391231.51 | 204331.52 | 20230204-165802_046f84fc-1da3-4660-84d7-121831a90fdd | 10.6678
20.84 | 30.55 | 5668.74 | 7.57 | [49.73, 73.39] | [19.95, 0.82] | [5.72, 5.72] | [10.0, 14.53] | 0 | 1047.73 | 75.4 | 79.93 | -4.53 | 7.42 | 90.9 | 80 | 19.2 | 9.71 | 16.76 | 4.08 | 5.41 | 3627.99 | 1068.94 | 1177.64 | 743.83 | 5.19 | 1.55 | 4.48 | 70.4 | 490 | 4700 | 69.81 | 0.47 | 15.83 | 23.36 | 60 | 9 | 9 | 0.97 | 294 | 302.72 | 394806.35 | 227065.5 | 20230204-165802_48dbed83-c165-48f4-b25c-bc3300aa41a1 | 9.5742
20.68 | 30.4 | 5656.69 | 7.59 | [21.0, 37.18] | [20.07, 1.26] | [5.76, 5.76] | [10.0, 7.37] | 0 | 742.62 | 46.83 | 44.2 | 2.63 | 7.18 | 92.17 | 87 | 18.6 | 9.72 | 17.03 | 3.65 | 7.62 | 3620.28 | 1073.23 | 1259.23 | 761.46 | 6.36 | 1.59 | 4.4 | 72.7 | 490 | 4700 | 69.91 | 0.47 | 10.56 | 46.1 | 60 | 9 | 9 | 0.49 | 294 | 298.42 | 371139.34 | 127849.72 | 20230204-165802_2c91f3ca-5286-4a2e-ba04-95f0b8de2859 | 13.8864
20.67 | 30.33 | 5541.51 | 7.6 | [54.25, 78.53] | [20.03, 1.3] | [5.71, 5.71] | [10.01, 15.55] | 0 | 1074.58 | 79.99 | 85.54 | -5.55 | 7.44 | 91.98 | 64 | 20.7 | 9.67 | 16.16 | 4.51 | 5.16 | 3546.57 | 1044.52 | 1145.93 | 725.91 | 5.14 | 1.55 | 4.5 | 68.2 | 490 | 4700 | 69.52 | 0.47 | 16.72 | 21.83 | 60 | 9 | 9 | 1.04 | 294 | 303.33 | 399913.67 | 247742.1 | 20230204-165802_0f7d7f89-c0d1-4098-b821-85ce886c8d82 | 8.6856
20.75 | 30.39 | 5543.31 | 7.6 | [52.79, 76.54] | [20.01, 1.41] | [5.42, 5.42] | [10.01, 15.16] | 0 | 1069.1 | 78.22 | 83.37 | -5.15 | 7.43 | 91.77 | 64 | 20.1 | 9.64 | 15.61 | 5.14 | 5.19 | 3547.72 | 1044.65 | 1145.25 | 725.71 | 5.16 | 1.55 | 4.5 | 65.24 | 490 | 4700 | 69.31 | 0.47 | 16.56 | 22.4 | 60 | 9 | 9 | 1.01 | 294 | 303.09 | 398092.6 | 243110.89 | 20230204-165802_f7152b24-dade-4b2f-a908-ae9ed2bf1916 | 8.846
20.63 | 30.31 | 5538.74 | 7.59 | [48.35, 72.95] | [20.02, 0.65] | [5.86, 5.86] | [9.22, 14.45] | 0 | 1036.21 | 74.23 | 79.46 | -5.23 | 7.41 | 91.85 | 63 | 20.6 | 9.68 | 15.94 | 4.69 | 5.35 | 3544.79 | 1044.72 | 1153.74 | 727.56 | 5.14 | 1.55 | 4.5 | 67.34 | 490 | 4700 | 69.6 | 0.47 | 16.02 | 23.5 | 60 | 9 | 9 | 0.96 | 294 | 302.67 | 386693.1 | 223779.88 | 20230204-165802_cce58037-06c7-4a8f-ac9b-6477d5d91f1a | 9.2987
20.35 | 29.97 | 5496.46 | 7.61 | [37.02, 56.43] | [20.06, 4.96] | [5.74, 5.74] | [6.88, 11.19] | 0 | 946.12 | 62.82 | 67.13 | -4.31 | 7.34 | 92.24 | 62 | 20.5 | 9.62 | 15.72 | 4.63 | 5.81 | 3517.73 | 1038.09 | 1163.01 | 726.04 | 5.61 | 1.56 | 4.49 | 67.47 | 490 | 4700 | 69.15 | 0.47 | 14.38 | 30.35 | 60 | 9 | 9 | 0.75 | 294 | 300.71 | 353374.76 | 228910.01 | 20230204-165802_59065f76-cfd4-413d-a65a-cbdf29b6e001 | 7.1042
21.14 | 30.56 | 5604.14 | 7.61 | [29.78, 45.92] | [19.98, 2.94] | [5.74, 5.74] | [10.0, 9.1] | 0 | 869.8 | 55.5 | 54.6 | 0.9 | 7.28 | 92.64 | 83 | 18.9 | 9.42 | 16.84 | 4.3 | 6.44 | 3586.65 | 1060.02 | 1205.85 | 744.88 | 6.1 | 1.6 | 4.41 | 68.63 | 490 | 4700 | 67.71 | 0.47 | 12.44 | 37.31 | 60 | 9 | 9 | 0.61 | 294 | 299.46 | 377845.68 | 173778 | 20230204-165802_f7f43ea9-5675-4faa-a1dd-42022485d25e | 11.6477
20.67 | 30.24 | 5533.12 | 7.61 | [54.32, 81.2] | [19.9, 1.91] | [5.35, 5.35] | [7.2, 16.08] | 0 | 1080.26 | 79.57 | 88.46 | -8.89 | 7.44 | 92.12 | 69 | 20.1 | 9.57 | 16.25 | 4.42 | 5.12 | 3541.2 | 1042.53 | 1140.82 | 723.82 | 4.95 | 1.55 | 4.5 | 68.39 | 490 | 4700 | 68.81 | 0.47 | 16.69 | 21.11 | 60 | 9 | 9 | 1.07 | 294 | 303.65 | 369516.34 | 262687.34 | 20230204-165802_e376ac16-adb0-42f1-b114-5a1e16710594 | 6.0975
20.97 | 30.51 | 5585.15 | 7.6 | [33.19, 54.93] | [19.89, 4.78] | [5.63, 5.63] | [4.26, 10.89] | 0 | 911.25 | 58.71 | 65.34 | -6.63 | 7.31 | 92.26 | 77 | 19.7 | 9.54 | 16.87 | 4.1 | 6.13 | 3574.5 | 1055.41 | 1189.61 | 739.48 | 5.39 | 1.58 | 4.45 | 69.91 | 490 | 4700 | 68.57 | 0.47 | 13.37 | 31.18 | 60 | 9 | 9 | 0.73 | 294 | 300.53 | 321269.8 | 222353.57 | 20230204-165802_d136b641-334d-4e33-8270-2e0107193261 | 5.6459
21.16 | 30.67 | 5619.42 | 7.6 | [29.54, 47.15] | [20.12, 3.77] | [5.16, 5.16] | [8.09, 9.35] | 0 | 870.83 | 54.82 | 56.08 | -1.26 | 7.27 | 91.83 | 76 | 19.7 | 9.51 | 16.75 | 4.42 | 6.45 | 3596.43 | 1061.76 | 1200.7 | 744.23 | 5.87 | 1.58 | 4.43 | 68.3 | 490 | 4700 | 68.4 | 0.47 | 12.54 | 36.33 | 60 | 9 | 9 | 0.62 | 294 | 299.61 | 359379.13 | 187019.24 | 20230204-165802_a9d867fd-059a-49c4-b4c6-f5974bd1e860 | 9.8379
21.58 | 31.16 | 6000.56 | 7.59 | [39.17, 71.38] | [25.02, 0.04] | [6.32, 6.32] | [6.9, 14.13] | 0 | 894.85 | 70.51 | 77.74 | -7.23 | 7.29 | 91.73 | 72 | 20.9 | 9.58 | 17.37 | 4.21 | 6.71 | 3840.36 | 1133.16 | 1274.6 | 792.94 | 4.99 | 1.64 | 4.32 | 69.49 | 490 | 4700 | 68.88 | 0.47 | 12.07 | 24.03 | 60 | 9 | 9 | 0.94 | 294 | 302.48 | 416863.53 | 212149.93 | 20230204-170424_54b7406b-43da-4c52-8fcd-f02c96498806 | 11.6846
21.76 | 31.23 | 5680.23 | 7.59 | [38.04, 67.71] | [25.01, 5.89] | [6.94, 6.94] | [2.87, 13.42] | 0 | 879.22 | 69.99 | 80.54 | -10.55 | 7.28 | 91.89 | 83 | 19.7 | 9.46 | 17.61 | 4.15 | 6.46 | 3635.35 | 1073.85 | 1216.98 | 753.56 | 5.21 | 1.6 | 4.4 | 69.5 | 490 | 4700 | 68.05 | 0.47 | 12.46 | 25.3 | 60 | 9 | 9 | 0.89 | 294 | 302.05 | 375346.83 | 274039.19 | 20230204-170424_9a50a1da-46a2-4735-a07c-50b260a7aa24 | 5.7824
22.22 | 31.86 | 5922.27 | 7.58 | [32.29, 62.1] | [24.98, 5.48] | [6.29, 6.29] | [2.0, 12.31] | 0 | 825.77 | 63.56 | 73.87 | -10.31 | 7.23 | 92.42 | 79 | 20.9 | 9.64 | 18.27 | 3.95 | 7.17 | 3790.25 | 1119.74 | 1276.97 | 786.75 | 5.16 | 1.64 | 4.3 | 70.94 | 490 | 4700 | 69.33 | 0.47 | 11.23 | 27.58 | 60 | 9 | 9 | 0.82 | 294 | 301.39 | 360487.55 | 252201.69 | 20230204-170424_a11df79a-fc8a-4c36-a17b-adaccff252b7 | 6.1807
21.97 | 31.53 | 5982.23 | 7.61 | [23.84, 53.59] | [24.97, 3.85] | [6.29, 6.29] | [2.0, 10.62] | 0 | 716.4 | 55.1 | 63.73 | -8.63 | 7.14 | 91.88 | 84 | 19.8 | 9.56 | 17.83 | 4.14 | 8.35 | 3828.63 | 1133.87 | 1328.34 | 803.18 | 5.19 | 1.68 | 4.25 | 69.77 | 490 | 4700 | 68.74 | 0.47 | 9.35 | 31.97 | 60 | 9 | 9 | 0.71 | 294 | 300.37 | 352936.7 | 207555.83 | 20230204-170424_b3dfb02b-0d82-43ed-89d6-16c4e5b19db6 | 8.298
22.17 | 31.65 | 5965.93 | 7.55 | [34.48, 71.76] | [25.24, 0.17] | [6.22, 6.22] | [2.0, 14.21] | 0 | 846.96 | 65.94 | 78.15 | -12.21 | 7.24 | 91.97 | 86 | 19.6 | 9.48 | 17.88 | 4.28 | 7.04 | 3818.2 | 1127.32 | 1278.53 | 790.67 | 4.64 | 1.61 | 4.33 | 68.89 | 490 | 4700 | 68.21 | 0.47 | 11.29 | 23.9 | 60 | 9 | 9 | 0.95 | 294 | 302.53 | 365473.36 | 214755.98 | 20230204-170424_1a46f6b8-1464-4cb7-87b0-f4933f8b8ee9 | 8.6026
21.52 | 31.08 | 5999.08 | 7.61 | [28.0, 57.7] | [24.99, 4.73] | [6.2, 6.2] | [2.0, 11.44] | 0 | 774.79 | 59.19 | 68.63 | -9.44 | 7.19 | 92.17 | 70 | 21.1 | 9.56 | 17.3 | 4.22 | 7.74 | 3839.41 | 1135.27 | 1308.66 | 800.14 | 5.17 | 1.67 | 4.27 | 69.38 | 490 | 4700 | 68.74 | 0.47 | 10.19 | 29.69 | 60 | 9 | 9 | 0.76 | 294 | 300.86 | 356760.96 | 230231.73 | 20230204-170424_45702f56-98ef-4175-821b-24c362c7ae69 | 7.222
21.99 | 31.67 | 5865.09 | 7.59 | [34.09, 64.49] | [24.99, 5.38] | [6.84, 6.84] | [2.0, 12.78] | 0 | 840.9 | 65.92 | 76.71 | -10.79 | 7.25 | 91.79 | 83 | 19.4 | 9.67 | 17.32 | 4.67 | 6.97 | 3753.66 | 1109.51 | 1266.78 | 780.29 | 5.16 | 1.63 | 4.32 | 67.43 | 490 | 4700 | 69.56 | 0.47 | 11.64 | 26.56 | 60 | 9 | 9 | 0.85 | 294 | 301.67 | 362611.07 | 258316.16 | 20230204-170424_adf315d3-4bd4-47b8-9fb0-3bea9cab5887 | 5.9529
22.04 | 31.79 | 5909.8 | 7.61 | [47.73, 87.09] | [25.04, 0.93] | [6.84, 6.84] | [2.0, 17.25] | 0 | 960.1 | 79.61 | 94.86 | -15.25 | 7.35 | 91.87 | 70 | 21.9 | 9.75 | 18.05 | 3.99 | 6.16 | 3782.27 | 1115.51 | 1244.25 | 778.97 | 4.62 | 1.65 | 4.31 | 70.95 | 490 | 4700 | 70.12 | 0.47 | 13.6 | 19.69 | 60 | 9 | 9 | 1.15 | 294 | 304.35 | 375268.41 | 268934.34 | 20230204-170424_91035fab-2679-43fb-8bff-4fe8414e0a73 | 6.0693
22.13 | 31.67 | 5780 | 7.59 | [24.29, 54.49] | [24.95, 3.55] | [6.75, 6.75] | [2.0, 10.8] | 0 | 719.86 | 55.99 | 64.79 | -8.8 | 7.16 | 92.3 | 85 | 19.8 | 9.55 | 17.96 | 4.17 | 8.03 | 3699.2 | 1096.47 | 1289.57 | 778.13 | 5.19 | 1.64 | 4.31 | 69.58 | 490 | 4700 | 68.64 | 0.47 | 9.76 | 31.44 | 60 | 9 | 9 | 0.72 | 294 | 300.48 | 353518.46 | 206962.87 | 20230204-170424_403ce1e5-02dc-4995-9410-f179587df1b6 | 8.365
21.98 | 31.47 | 5717.92 | 7.61 | [29.71, 60.15] | [24.92, 4.4] | [6.99, 6.99] | [2.0, 11.92] | 0 | 790.72 | 61.62 | 71.54 | -9.92 | 7.22 | 92.15 | 85 | 19.5 | 9.48 | 17.66 | 4.32 | 7.23 | 3659.47 | 1083.18 | 1253.01 | 764.98 | 5.17 | 1.64 | 4.33 | 68.7 | 490 | 4700 | 68.19 | 0.47 | 10.94 | 28.48 | 60 | 9 | 9 | 0.79 | 294 | 301.15 | 358097.98 | 233881.78 | 20230204-170424_43d46bff-d2dc-423d-8a07-53fc2cd2d5cb | 7.09
21.46 | 31.07 | 5986.02 | 7.6 | [44.42, 73.54] | [25.04, 0.48] | [6.07, 6.07] | [10.01, 14.56] | 0 | 941.4 | 75.53 | 80.09 | -4.56 | 7.32 | 91.84 | 67 | 21 | 9.6 | 16.82 | 4.64 | 6.36 | 3831.05 | 1129.25 | 1257.66 | 787.73 | 5.19 | 1.64 | 4.32 | 67.43 | 490 | 4700 | 69.06 | 0.47 | 12.89 | 23.32 | 60 | 9 | 9 | 0.97 | 294 | 302.74 | 453035 | 223606.04 | 20230204-170424_5fbf016b-9724-4156-858a-b9c47159f7f2 | 13.0953
21.91 | 31.65 | 5908.62 | 7.64 | [33.61, 63.64] | [24.74, 5.33] | [6.73, 6.73] | [2.0, 12.62] | 0 | 839.7 | 65.08 | 75.7 | -10.62 | 7.25 | 91.74 | 73 | 21.1 | 9.74 | 17.69 | 4.22 | 7.04 | 3781.52 | 1117.7 | 1276 | 785.98 | 5.16 | 1.69 | 4.26 | 69.78 | 490 | 4700 | 70.06 | 0.47 | 11.61 | 26.92 | 60 | 9 | 9 | 0.84 | 294 | 301.57 | 359081.4 | 255176.81 | 20230204-170424_fa6294b6-2f51-4461-b156-ad963cb3ab95 | 5.9306
21.92 | 31.46 | 5976.64 | 7.59 | [37.01, 74.2] | [25.06, 0.56] | [6.06, 6.06] | [2.0, 14.69] | 0 | 876.16 | 68.13 | 80.82 | -12.69 | 7.27 | 91.86 | 85 | 19.4 | 9.55 | 17.57 | 4.35 | 6.82 | 3825.05 | 1128.58 | 1271.43 | 789.89 | 4.64 | 1.64 | 4.31 | 68.7 | 490 | 4700 | 68.67 | 0.47 | 11.8 | 23.11 | 60 | 9 | 9 | 0.98 | 294 | 302.82 | 365333.97 | 226418.78 | 20230204-170424_3098fa35-14be-4597-88a1-0d6057d5753d | 7.9289
22.04 | 31.59 | 5962.65 | 7.6 | [30.08, 59.88] | [24.99, 5.06] | [6.28, 6.28] | [2.0, 11.87] | 0 | 800.03 | 61.35 | 71.22 | -9.87 | 7.21 | 92.17 | 81 | 20.1 | 9.55 | 17.75 | 4.29 | 7.45 | 3816.1 | 1127.93 | 1293.55 | 793.83 | 5.17 | 1.67 | 4.27 | 69.03 | 490 | 4700 | 68.69 | 0.47 | 10.64 | 28.61 | 60 | 9 | 9 | 0.79 | 294 | 301.12 | 358684.59 | 240668.61 | 20230204-170424_2d126446-68db-4688-afa5-5b4affe3d0bd | 6.7361
21.62 | 31.18 | 5982.75 | 7.6 | [30.5, 60.29] | [24.96, 5.12] | [6.3, 6.3] | [2.0, 11.95] | 0 | 805.31 | 61.76 | 71.71 | -9.95 | 7.21 | 91.99 | 73 | 20.5 | 9.56 | 17.13 | 4.49 | 7.43 | 3828.96 | 1131.66 | 1296.56 | 796.24 | 5.17 | 1.66 | 4.29 | 68.06 | 490 | 4700 | 68.78 | 0.47 | 10.7 | 28.41 | 60 | 9 | 9 | 0.8 | 294 | 301.17 | 358620.59 | 242602.23 | 20230204-170424_9be8e52a-556d-4e62-bb92-66462da13b61 | 6.6221
22.21 | 31.8 | 5834.27 | 7.6 | [18.21, 48.53] | [25.23, 2.53] | [6.64, 6.64] | [2.0, 9.62] | 0 | 617.5 | 50.08 | 57.7 | -7.62 | 7.07 | 91.92 | 86 | 19.7 | 9.59 | 17.98 | 4.23 | 9.45 | 3733.93 | 1109.93 | 1346.68 | 795.17 | 5.21 | 1.67 | 4.25 | 69.39 | 490 | 4700 | 68.93 | 0.47 | 8.16 | 35.31 | 60 | 9 | 9 | 0.64 | 294 | 299.77 | 351450.7 | 177037.15 | 20230204-170424_1be70015-0bd5-408c-b698-70e5caad58e7 | 9.9551

## N2
supply_temp | return_temp | ct_conductivity | ct_ph | Bore | CWRO | BoilerBD | BD | scheme | mu_conductivity | mu_flow(PV) | mu-flow(OV) | m-Saving(PV-OV) | mu_ph | cooling_tower_level | relative_humidity | ambient_temp | delta_temp | wetBulb_temp | approach_temp | cond_coc | ct_tds | ct_ca | ct_alk | ct_chloride | flow_cycle | sat_index | sta_index | perf_index | system_vol | rec_rate | evap_loss | drift_loss | blowdown_coc | hold_time_index | dosing_residual | dosing_contact_time | dosing_density | dosing_continuous | dosing_initial | dosing_slug | currentOperatingCost | newOperatingCost | updatedDateTime | 1744.567
20.17 | 29.44 | 5519.29 | 7.6 | [27.45, 37.42] | [25.01, 16.97] | [12.72, 12.72] | [5.53, 7.46] | 0 | 720.49 | 65.18 | 67.11 | -1.93 | 7.26 | 89.99 | 44 | 22.5 | 9.27 | 14.96 | 5.21 | 7.66 | 3532.34 | 1057.76 | 1309.44 | 768.06 | 8.74 | 1.61 | 4.39 | 64.05 | 680 | 5900 | 83.72 | 0.59 | 12.57 | 63.2 | 60 | 9 | 9 | 0.5 | 408 | 412.47 | 398066.87 | 327776.82 | 20230204-160652_2002ecfe-bd5b-4d66-b73c-bc6b1d75d014 | 4.012
19.92 | 29.26 | 5530.14 | 7.6 | [27.13, 31.52] | [24.86, 22.04] | [12.61, 12.61] | [4.73, 6.3] | 0 | 718.65 | 64.6 | 66.17 | -1.57 | 7.26 | 89.87 | 46 | 21.7 | 9.34 | 14.59 | 5.33 | 7.7 | 3539.29 | 1059.9 | 1312.73 | 769.74 | 10.25 | 1.6 | 4.39 | 63.67 | 680 | 5900 | 84.33 | 0.59 | 12.6 | 74.77 | 60 | 9 | 9 | 0.42 | 408 | 411.78 | 387772.03 | 373068.96 | 20230204-160652_99555fc7-8c3b-4882-a6f7-4504d0b92880 | 0.83922
20.48 | 29.79 | 5507.58 | 7.6 | [28.59, 28.28] | [24.91, 24.56] | [12.34, 12.34] | [6.32, 5.67] | 0 | 738.07 | 65.84 | 65.18 | 0.66 | 7.27 | 89.96 | 63 | 19.9 | 9.31 | 15.3 | 5.18 | 7.46 | 3524.85 | 1054.04 | 1292.93 | 762.67 | 11.62 | 1.6 | 4.4 | 64.24 | 680 | 5900 | 84 | 0.59 | 13 | 83.13 | 60 | 9 | 9 | 0.38 | 408 | 411.4 | 405628.19 | 394440.42 | 20230204-160652_112b7c4b-48f6-4fee-9835-c897f50db736 | 0.63857
20.81 | 30.05 | 5502.47 | 7.6 | [21.5, 23.7] | [25.01, 20.96] | [12.35, 12.35] | [6.61, 4.75] | 0 | 640.37 | 58.86 | 57.01 | 1.85 | 7.2 | 89.97 | 87 | 17.2 | 9.24 | 15.66 | 5.15 | 8.59 | 3521.58 | 1058.98 | 1353.35 | 777.74 | 12.39 | 1.63 | 4.33 | 64.18 | 680 | 5900 | 83.38 | 0.59 | 10.98 | 99.19 | 60 | 9 | 9 | 0.32 | 408 | 410.85 | 403586.25 | 336927.2 | 20230204-160652_e00046a6-6eb4-4c3d-a232-5e88faccf455 | 3.8047
20.31 | 29.58 | 5507.53 | 7.6 | [27.82, 27.85] | [25.02, 24.13] | [12.21, 12.21] | [6.45, 5.58] | 0 | 728.47 | 65.05 | 64.19 | 0.86 | 7.26 | 90.01 | 63 | 19.6 | 9.26 | 15.03 | 5.28 | 7.56 | 3524.82 | 1054.25 | 1296.14 | 763.35 | 11.66 | 1.6 | 4.39 | 63.69 | 680 | 5900 | 83.63 | 0.59 | 12.75 | 84.44 | 60 | 9 | 9 | 0.37 | 408 | 411.35 | 407441.32 | 387729.91 | 20230204-160652_fab0dbb8-028f-4138-acb0-0f679b3742bd | 1.1251
19.85 | 29.14 | 5493.38 | 7.6 | [28.09, 27.82] | [24.93, 24.14] | [12.17, 12.17] | [6.63, 5.58] | 0 | 732.97 | 65.19 | 64.13 | 1.06 | 7.26 | 90.01 | 68 | 17.8 | 9.29 | 13.99 | 5.86 | 7.49 | 3515.76 | 1051.31 | 1290.34 | 760.76 | 11.69 | 1.59 | 4.42 | 61.33 | 680 | 5900 | 83.86 | 0.59 | 12.91 | 84.5 | 60 | 9 | 9 | 0.37 | 408 | 411.35 | 408449.72 | 387795.77 | 20230204-160652_6eb5ef77-735c-4259-917e-f1e351772977 | 1.1789
20.43 | 29.66 | 5497.91 | 7.6 | [27.07, 30.54] | [24.97, 21.2] | [12.37, 12.37] | [6.4, 6.11] | 0 | 718.38 | 64.41 | 64.11 | 0.3 | 7.26 | 90.08 | 56 | 20.9 | 9.23 | 15.29 | 5.14 | 7.65 | 3518.66 | 1053.27 | 1301.87 | 764.21 | 10.55 | 1.6 | 4.39 | 64.21 | 680 | 5900 | 83.3 | 0.59 | 12.52 | 77.18 | 60 | 9 | 9 | 0.41 | 408 | 411.66 | 405777.71 | 359651.72 | 20230204-160652_d3ca2bbe-cc61-4fde-8bfc-9ffe281ed7a3 | 2.6328
20.5 | 29.77 | 5504.15 | 7.6 | [30.3, 34.05] | [25.08, 21.65] | [12.33, 12.33] | [6.48, 6.8] | 0 | 756.85 | 67.71 | 68.03 | -0.32 | 7.28 | 89.95 | 50 | 21.9 | 9.27 | 15.33 | 5.16 | 7.27 | 3522.66 | 1052.27 | 1281 | 759.28 | 9.95 | 1.6 | 4.4 | 64.23 | 680 | 5900 | 83.69 | 0.59 | 13.34 | 69.27 | 60 | 9 | 9 | 0.45 | 408 | 412.08 | 410698.68 | 375275.97 | 20230204-160652_270e0bcf-5337-4ce8-af48-c8601e639e04 | 2.0218
19.95 | 29.21 | 5528.63 | 7.6 | [23.04, 29.86] | [25.09, 20.35] | [12.47, 12.47] | [3.88, 5.97] | 0 | 661.69 | 60.6 | 62.68 | -2.08 | 7.22 | 89.94 | 49 | 20.8 | 9.27 | 14.25 | 5.7 | 8.36 | 3538.32 | 1062.69 | 1345.65 | 777.88 | 10.15 | 1.61 | 4.37 | 61.92 | 680 | 5900 | 83.64 | 0.59 | 11.37 | 78.94 | 60 | 9 | 9 | 0.4 | 408 | 411.58 | 378292.06 | 347353.91 | 20230204-160652_39b8955b-2c79-4917-ac03-a0880fdbbd46 | 1.7659
20.45 | 29.68 | 5507.55 | 7.6 | [26.97, 48.67] | [24.94, 6.57] | [12.35, 12.35] | [6.33, 9.65] | 0 | 717.66 | 64.26 | 67.59 | -3.33 | 7.26 | 89.98 | 47 | 22.2 | 9.23 | 15.16 | 5.29 | 7.67 | 3524.83 | 1055.14 | 1304.41 | 765.61 | 6.66 | 1.61 | 4.38 | 63.56 | 680 | 5900 | 83.36 | 0.59 | 12.49 | 48.81 | 60 | 9 | 9 | 0.64 | 408 | 413.79 | 404655.52 | 232106.18 | 20230204-160652_c45e770a-13ee-47de-8283-022dba0e284a | 9.8487
19.95 | 29.24 | 5501.99 | 7.6 | [28.48, 29.63] | [25.02, 23.1] | [12.51, 12.51] | [6.7, 5.93] | 0 | 734.55 | 66.01 | 65.24 | 0.77 | 7.27 | 89.99 | 65 | 18.4 | 9.29 | 14.18 | 5.76 | 7.49 | 3521.27 | 1053.34 | 1294.86 | 762.81 | 11.13 | 1.59 | 4.41 | 61.72 | 680 | 5900 | 83.89 | 0.59 | 12.92 | 79.44 | 60 | 9 | 9 | 0.4 | 408 | 411.56 | 410930.29 | 380530.72 | 20230204-160652_d36adc95-942a-49a8-bced-44922c013e5e | 1.7351
20.68 | 29.92 | 5492.89 | 7.6 | [26.19, 28.69] | [25.09, 22.01] | [12.47, 12.47] | [6.32, 5.74] | 0 | 705.11 | 63.75 | 63.17 | 0.58 | 7.25 | 90.01 | 62 | 20.3 | 9.24 | 15.54 | 5.14 | 7.79 | 3515.45 | 1053.13 | 1308.96 | 765.67 | 11.1 | 1.62 | 4.37 | 64.27 | 680 | 5900 | 83.44 | 0.59 | 12.29 | 82.05 | 60 | 9 | 9 | 0.38 | 408 | 411.45 | 405875.66 | 364337.72 | 20230204-160652_0e42a183-e08c-4610-b39f-fa7f74843969 | 2.3709
20.72 | 29.87 | 5516.55 | 7.6 | [20.23, 21.17] | [25.02, 21.82] | [12.3, 12.3] | [6.51, 4.25] | 0 | 620.66 | 57.55 | 55.29 | 2.26 | 7.19 | 90.08 | 84 | 18.4 | 9.15 | 16.47 | 4.25 | 8.89 | 3530.59 | 1063.01 | 1370.92 | 783.3 | 13.53 | 1.64 | 4.32 | 68.29 | 680 | 5900 | 82.56 | 0.59 | 10.47 | 110.79 | 60 | 9 | 9 | 0.28 | 408 | 410.55 | 401523.33 | 340154.93 | 20230204-160652_c3b98b40-ab60-425a-bdda-7e718e56c562 | 3.5028
20.09 | 29.36 | 5505.53 | 7.6 | [27.77, 29.16] | [24.93, 22.74] | [12.31, 12.31] | [6.64, 5.84] | 0 | 728.05 | 65.01 | 64.21 | 0.8 | 7.26 | 90 | 64 | 18.8 | 9.28 | 14.43 | 5.66 | 7.56 | 3523.54 | 1054.13 | 1297.64 | 763.69 | 11.14 | 1.6 | 4.4 | 62.11 | 680 | 5900 | 83.74 | 0.59 | 12.76 | 80.72 | 60 | 9 | 9 | 0.39 | 408 | 411.5 | 408412.65 | 374504.95 | 20230204-160652_5abd403a-d726-45f8-b7e4-b4cdbe6cc1a9 | 1.9354
20.28 | 29.59 | 5495.08 | 7.61 | [30.2, 30.38] | [24.9, 24.34] | [12.2, 12.2] | [6.45, 6.08] | 0 | 758.41 | 67.3 | 66.92 | 0.38 | 7.28 | 90 | 53 | 21.4 | 9.31 | 15.32 | 4.96 | 7.25 | 3516.85 | 1050.4 | 1277.63 | 757.67 | 11.06 | 1.6 | 4.41 | 65.23 | 680 | 5900 | 84.05 | 0.59 | 13.46 | 77.46 | 60 | 9 | 9 | 0.41 | 408 | 411.65 | 407991.83 | 397687.78 | 20230204-160652_4eff511c-025f-4e1b-9331-9f4deb00d65a | 0.58813
20.18 | 29.35 | 5496.14 | 7.6 | [24.57, 29.13] | [24.95, 19.86] | [12.15, 12.15] | [6.36, 5.82] | 0 | 686.78 | 61.67 | 61.14 | 0.53 | 7.23 | 90.04 | 69 | 18.6 | 9.17 | 14.85 | 5.33 | 8 | 3517.53 | 1054.42 | 1318.02 | 768.05 | 10.59 | 1.61 | 4.38 | 63.25 | 680 | 5900 | 82.79 | 0.59 | 11.82 | 80.93 | 60 | 9 | 9 | 0.39 | 408 | 411.49 | 402870.59 | 338863.87 | 20230204-160652_4527b027-783a-4a3e-800c-f2dc34ec0830 | 3.6534
20.22 | 29.46 | 5523.73 | 7.6 | [27.95, 29.74] | [24.91, 23.22] | [12.54, 12.54] | [5.85, 5.95] | 0 | 729 | 65.4 | 65.5 | -0.1 | 7.27 | 89.99 | 44 | 22.6 | 9.25 | 15.05 | 5.17 | 7.58 | 3535.19 | 1057.93 | 1304.02 | 766.92 | 10.98 | 1.6 | 4.39 | 64.13 | 680 | 5900 | 83.46 | 0.59 | 12.69 | 79.15 | 60 | 9 | 9 | 0.4 | 408 | 411.57 | 400407.88 | 382251.88 | 20230204-160652_c5c6454b-51a1-4fda-aa0d-529316b48465 | 1.0363
19.96 | 29.22 | 5528.43 | 7.6 | [24.25, 41.37] | [25.06, 11.86] | [12.57, 12.57] | [4.3, 8.22] | 0 | 678.68 | 61.88 | 65.8 | -3.92 | 7.23 | 90.01 | 48 | 21 | 9.26 | 14.28 | 5.68 | 8.15 | 3538.2 | 1061.75 | 1335.59 | 775.37 | 7.52 | 1.61 | 4.38 | 62 | 680 | 5900 | 83.62 | 0.59 | 11.7 | 57.3 | 60 | 9 | 9 | 0.55 | 408 | 412.93 | 383312.43 | 276291.04 | 20230204-160652_43d4023c-0c77-4e81-b9d5-c8c178f24cb5 | 6.1085
19.89 | 29.17 | 5499.76 | 7.59 | [25.3, 24.4] | [25.11, 24.53] | [12.32, 12.32] | [6.38, 4.9] | 0 | 694.13 | 62.73 | 61.25 | 1.48 | 7.24 | 89.97 | 66 | 18.5 | 9.28 | 14.4 | 5.49 | 7.92 | 3519.85 | 1054.83 | 1315.41 | 767.74 | 12.8 | 1.6 | 4.4 | 62.81 | 680 | 5900 | 83.74 | 0.59 | 12.1 | 96.18 | 60 | 9 | 9 | 0.33 | 408 | 410.94 | 405712.57 | 382766.33 | 20230204-160652_74f0b3d5-caf9-4b5d-9a08-558e397f3fc9 | 1.3097
20.06 | 29.3 | 5527.82 | 7.6 | [27.21, 35.22] | [25.09, 18.91] | [12.62, 12.62] | [5.2, 7.03] | 0 | 717.3 | 64.92 | 66.75 | -1.83 | 7.26 | 90.03 | 45 | 22.2 | 9.25 | 14.86 | 5.19 | 7.71 | 3537.8 | 1059.37 | 1311.79 | 769.24 | 9.24 | 1.6 | 4.39 | 64.04 | 680 | 5900 | 83.48 | 0.59 | 12.45 | 67.07 | 60 | 9 | 9 | 0.47 | 408 | 412.22 | 395399.37 | 345170.89 | 20230204-160652_326510b5-793c-4963-82db-7429b7c8d3f9 | 2.8669
19.83 | 29.1 | 5496.86 | 7.6 | [27.84, 30.76] | [25.02, 21.56] | [12.26, 12.26] | [6.69, 6.15] | 0 | 728.3 | 65.12 | 64.58 | 0.54 | 7.26 | 90.01 | 66 | 18.1 | 9.27 | 14.03 | 5.8 | 7.55 | 3517.99 | 1052.3 | 1294.3 | 762.08 | 10.59 | 1.59 | 4.42 | 61.5 | 680 | 5900 | 83.65 | 0.59 | 12.78 | 76.62 | 60 | 9 | 9 | 0.41 | 408 | 411.69 | 410032.02 | 364634.68 | 20230204-160652_93b80a35-d03b-42cf-8cf3-91bfa591a408 | 2.5912
20.21 | 29.46 | 5520.47 | 7.6 | [30.49, 36.51] | [25.1, 20.18] | [12.53, 12.53] | [6.19, 7.29] | 0 | 757.45 | 68.12 | 69.22 | -1.1 | 7.28 | 89.94 | 44 | 22.9 | 9.25 | 15.3 | 4.91 | 7.29 | 3533.1 | 1055.63 | 1286.44 | 762.07 | 9.35 | 1.6 | 4.4 | 65.33 | 680 | 5900 | 83.52 | 0.59 | 13.28 | 64.68 | 60 | 9 | 9 | 0.49 | 408 | 412.37 | 408417.13 | 364457.95 | 20230204-160652_a2aa0c9a-f8b5-486a-af18-6b7e3297075c | 2.5091
20.57 | 29.79 | 5500.33 | 7.6 | [24.55, 26.36] | [24.99, 21.84] | [12.52, 12.52] | [6.62, 5.28] | 0 | 683.81 | 62.06 | 60.72 | 1.34 | 7.24 | 89.95 | 86 | 17.1 | 9.22 | 15.45 | 5.12 | 8.04 | 3520.21 | 1056.02 | 1325.39 | 770.55 | 11.75 | 1.62 | 4.36 | 64.3 | 680 | 5900 | 83.26 | 0.59 | 11.82 | 89.25 | 60 | 9 | 9 | 0.35 | 408 | 411.17 | 406234.01 | 355521.84 | 20230204-160652_f8fc4306-d166-453b-8e33-a2ee021bbac5 | 2.8945
20.44 | 29.65 | 5499 | 7.6 | [28.3, 34.97] | [24.98, 18.93] | [12.38, 12.38] | [6.35, 6.98] | 0 | 733.58 | 65.66 | 66.28 | -0.62 | 7.27 | 90.08 | 46 | 22.2 | 9.21 | 15.01 | 5.43 | 7.5 | 3519.36 | 1052.66 | 1293.52 | 762.16 | 9.41 | 1.6 | 4.39 | 62.93 | 680 | 5900 | 83.15 | 0.59 | 12.8 | 67.54 | 60 | 9 | 9 | 0.47 | 408 | 412.19 | 406476.87 | 344544 | 20230204-160652_7992da71-1662-43de-ae95-8d1b6fd30c32 | 3.535
19.85 | 29.13 | 5488.75 | 7.6 | [24.12, 27.57] | [25.05, 20.64] | [12.47, 12.47] | [6.47, 5.52] | 0 | 677.52 | 61.64 | 60.68 | 0.96 | 7.23 | 90.06 | 68 | 17.8 | 9.28 | 13.99 | 5.86 | 8.1 | 3512.8 | 1054.04 | 1325.6 | 769.63 | 11.17 | 1.61 | 4.39 | 61.32 | 680 | 5900 | 83.8 | 0.59 | 11.8 | 85.43 | 60 | 9 | 9 | 0.37 | 408 | 411.31 | 404916.32 | 344309.41 | 20230204-160652_a922fd44-3964-4aa1-8c28-94ef9c927970 | 3.4593
20.21 | 29.47 | 5506.62 | 7.6 | [27.93, 26.6] | [25.07, 25.16] | [12.29, 12.29] | [6.56, 5.34] | 0 | 728.68 | 65.29 | 64.05 | 1.24 | 7.26 | 90.01 | 63 | 19.3 | 9.26 | 14.76 | 5.45 | 7.56 | 3524.24 | 1054.16 | 1296.47 | 763.41 | 12.23 | 1.6 | 4.4 | 62.95 | 680 | 5900 | 83.6 | 0.59 | 12.75 | 88.28 | 60 | 9 | 9 | 0.36 | 408 | 411.2 | 409357.17 | 396932.01 | 20230204-160652_21b5fbc6-6c83-4713-9b12-4d34ca9034c0 | 0.7092
20.67 | 30 | 5474.5 | 7.6 | [23.28, 50.11] | [25.2, 2.13] | [12.29, 12.29] | [6.17, 9.93] | 0 | 665.2 | 60.77 | 64.53 | -3.76 | 7.22 | 90.03 | 86 | 16.8 | 9.33 | 15.15 | 5.52 | 8.23 | 3503.68 | 1051.65 | 1327.09 | 768.69 | 6.12 | 1.62 | 4.36 | 62.84 | 680 | 5900 | 84.24 | 0.59 | 11.65 | 47.47 | 60 | 9 | 9 | 0.66 | 408 | 413.96 | 402866.35 | 181635.35 | 20230204-161315_91352dc8-45fd-49f7-87fc-1fac06cdd8b8 | 12.6273
22.66 | 31.91 | 5521.31 | 7.6 | [29.95, 37.74] | [24.5, 17.62] | [12.34, 12.34] | [6.62, 7.52] | 0 | 758.85 | 66.79 | 67.7 | -0.91 | 7.29 | 89.84 | 70 | 22.6 | 9.25 | 18.7 | 3.95 | 7.28 | 3533.64 | 1055.88 | 1287.04 | 762.36 | 8.88 | 1.65 | 4.31 | 70.06 | 680 | 5900 | 83.52 | 0.59 | 13.31 | 62.65 | 60 | 9 | 9 | 0.5 | 408 | 412.51 | 404833.65 | 336406.42 | 20230204-161315_c18632b4-4ec0-4111-9546-4b496a50f4e3 | 3.9057
20.57 | 29.79 | 5465.66 | 7.59 | [20.04, 50.06] | [24.8, 2.03] | [12.37, 12.37] | [2.67, 9.92] | 0 | 619.41 | 57.21 | 64.46 | -7.25 | 7.19 | 90.01 | 79 | 17 | 9.22 | 14.53 | 6.04 | 8.82 | 3498.02 | 1053.67 | 1361.93 | 777.18 | 5.77 | 1.62 | 4.35 | 60.42 | 680 | 5900 | 83.2 | 0.59 | 10.63 | 47.52 | 60 | 9 | 9 | 0.66 | 408 | 413.95 | 359675.1 | 180375.51 | 20230204-161315_ac5da114-592c-44bf-a45d-3aa379063127 | 10.234
20.43 | 29.67 | 5539.37 | 7.6 | [22.72, 52.37] | [25.06, 2.78] | [12.3, 12.3] | [3.01, 10.38] | 0 | 658.42 | 60.08 | 67.45 | -7.37 | 7.22 | 89.92 | 81 | 17.8 | 9.24 | 15.54 | 4.89 | 8.41 | 3545.2 | 1064.69 | 1348.46 | 779.31 | 5.79 | 1.62 | 4.35 | 65.38 | 680 | 5900 | 83.4 | 0.59 | 11.25 | 45.42 | 60 | 9 | 9 | 0.69 | 408 | 414.23 | 368540.94 | 196201.56 | 20230204-161315_337ac0c4-cca7-4eb2-ae61-2531d62b51af | 9.8367
21.25 | 30.39 | 5538.09 | 7.6 | [19.91, 48.94] | [25.1, 1.6] | [12.47, 12.47] | [4.17, 9.69] | 0 | 613.83 | 57.48 | 63.01 | -5.53 | 7.19 | 89.98 | 76 | 19.9 | 9.14 | 16.94 | 4.31 | 9.02 | 3544.38 | 1067.96 | 1383.73 | 788.4 | 5.93 | 1.65 | 4.3 | 67.94 | 680 | 5900 | 82.53 | 0.59 | 10.29 | 48.61 | 60 | 9 | 9 | 0.65 | 408 | 413.82 | 378507.85 | 171940.69 | 20230204-161315_020ccc41-143d-4620-b7f7-e36c202f57e7 | 11.7904
20.44 | 29.67 | 5451.82 | 7.6 | [27.98, 33.61] | [24.74, 21.21] | [12.32, 12.32] | [4.61, 6.71] | 0 | 732.57 | 65.04 | 67.14 | -2.1 | 7.27 | 89.93 | 82 | 16.7 | 9.24 | 14.59 | 5.84 | 7.44 | 3489.17 | 1043.77 | 1283.62 | 755.97 | 9.69 | 1.6 | 4.41 | 61.25 | 680 | 5900 | 83.4 | 0.59 | 12.95 | 70.18 | 60 | 9 | 9 | 0.45 | 408 | 412.03 | 385571.95 | 368568.98 | 20230204-161315_c9d3decf-a54e-412b-8ef8-74b7809bf909 | 0.97049
20.28 | 29.5 | 5460.15 | 7.6 | [21.18, 30.79] | [25.0, 18.32] | [12.37, 12.37] | [3.22, 6.15] | 0 | 635.46 | 58.55 | 61.48 | -2.93 | 7.2 | 90.06 | 78 | 16.9 | 9.22 | 14.32 | 5.96 | 8.59 | 3494.5 | 1051.22 | 1346.81 | 772.77 | 9.52 | 1.62 | 4.36 | 60.71 | 680 | 5900 | 83.19 | 0.59 | 10.96 | 76.65 | 60 | 9 | 9 | 0.41 | 408 | 411.69 | 368798.15 | 324976.43 | 20230204-161315_c0f709e6-9c3e-497a-add1-63f302d9413a | 2.5012
22.66 | 31.81 | 5528.59 | 7.6 | [24.35, 46.72] | [25.0, 5.69] | [12.45, 12.45] | [6.21, 9.27] | 0 | 681.46 | 61.8 | 64.86 | -3.06 | 7.23 | 89.99 | 78 | 21.6 | 9.15 | 18.81 | 3.86 | 8.11 | 3538.29 | 1061.46 | 1332.75 | 774.59 | 6.67 | 1.66 | 4.27 | 70.34 | 680 | 5900 | 82.56 | 0.59 | 11.61 | 50.86 | 60 | 9 | 9 | 0.62 | 408 | 413.56 | 401882.62 | 215797.02 | 20230204-161315_44539f67-e12a-4365-a761-45da7ef788f4 | 10.6213
20.84 | 30.05 | 5470.25 | 7.6 | [19.7, 50.47] | [25.15, 2.2] | [12.33, 12.33] | [2.19, 10.0] | 0 | 610.68 | 57.18 | 65 | -7.82 | 7.18 | 90.03 | 73 | 19.3 | 9.21 | 16 | 4.85 | 8.96 | 3500.96 | 1054.76 | 1366.64 | 778.54 | 5.72 | 1.63 | 4.33 | 65.52 | 680 | 5900 | 83.13 | 0.59 | 10.45 | 47.13 | 60 | 9 | 9 | 0.67 | 408 | 414 | 358822.51 | 183562.15 | 20230204-161315_abeba2c6-e346-4579-9497-9f57a5a2e960 | 10.0034
20.78 | 29.95 | 5493.99 | 7.59 | [20.01, 42.72] | [25.01, 4.2] | [12.38, 12.38] | [6.58, 8.47] | 0 | 616.86 | 57.4 | 59.3 | -1.9 | 7.19 | 90.07 | 87 | 17 | 9.16 | 15.46 | 5.32 | 8.91 | 3516.16 | 1059.11 | 1369.48 | 781.24 | 6.78 | 1.63 | 4.33 | 63.27 | 680 | 5900 | 82.7 | 0.59 | 10.46 | 55.64 | 60 | 9 | 9 | 0.56 | 408 | 413.08 | 402051.74 | 185782.13 | 20230204-161315_41eeefb3-8790-454e-93c1-b3a04ffe9dd2 | 12.3442
19.95 | 29.24 | 5516.57 | 7.6 | [16.69, 32.53] | [24.82, 13.31] | [12.47, 12.47] | [2.15, 6.48] | 0 | 561.64 | 53.98 | 58.31 | -4.33 | 7.16 | 90.08 | 84 | 16.5 | 9.29 | 14.63 | 5.32 | 9.82 | 3530.61 | 1068.55 | 1426.43 | 797.83 | 8.33 | 1.64 | 4.32 | 63.6 | 680 | 5900 | 83.87 | 0.59 | 9.51 | 72.74 | 60 | 9 | 9 | 0.43 | 408 | 411.89 | 351806.6 | 268464.75 | 20230204-161315_90fcb8fb-987a-45e6-86ab-f76005e7639b | 4.757
20.98 | 30.2 | 5486.79 | 7.6 | [19.42, 50.32] | [24.87, 1.93] | [12.54, 12.54] | [2.0, 9.97] | 0 | 607.78 | 56.83 | 64.79 | -7.96 | 7.19 | 90.01 | 86 | 16 | 9.23 | 14.37 | 6.6 | 9.03 | 3511.54 | 1058.93 | 1378.62 | 783.26 | 5.7 | 1.64 | 4.31 | 58.28 | 680 | 5900 | 83.28 | 0.59 | 10.37 | 47.28 | 60 | 9 | 9 | 0.66 | 408 | 413.98 | 353300.4 | 180079.59 | 20230204-161315_17c1cd67-cae8-437a-9652-d5c19437b078 | 9.887
22.1 | 31.27 | 5532.53 | 7.6 | [24.95, 41.02] | [25.0, 11.85] | [12.38, 12.38] | [5.23, 8.16] | 0 | 690.05 | 62.33 | 65.25 | -2.92 | 7.24 | 89.95 | 74 | 21.5 | 9.17 | 18.2 | 3.9 | 8.02 | 3540.82 | 1061.55 | 1327.17 | 773.4 | 7.64 | 1.65 | 4.3 | 70.14 | 680 | 5900 | 82.79 | 0.59 | 11.8 | 57.78 | 60 | 9 | 9 | 0.54 | 408 | 412.89 | 392513.85 | 274964.44 | 20230204-161315_8eee0256-59bc-4ce3-a30a-5382b8e20255 | 6.7094
22.36 | 31.54 | 5534.5 | 7.6 | [24.41, 28.17] | [25.0, 21.13] | [12.7, 12.7] | [5.74, 5.64] | 0 | 680.63 | 62.11 | 62 | 0.11 | 7.24 | 90.03 | 77 | 21.4 | 9.17 | 18.49 | 3.87 | 8.13 | 3542.08 | 1063.08 | 1337.87 | 776.57 | 11.02 | 1.66 | 4.28 | 70.31 | 680 | 5900 | 82.81 | 0.59 | 11.61 | 83.61 | 60 | 9 | 9 | 0.38 | 408 | 411.38 | 397453.02 | 352238.33 | 20230204-161315_5e25c133-a876-4251-b978-b5a07e0a77bd | 2.5807
20.22 | 29.5 | 5477.73 | 7.6 | [20.97, 33.04] | [25.0, 13.7] | [12.48, 12.48] | [5.81, 6.58] | 0 | 631.61 | 58.45 | 59.22 | -0.77 | 7.2 | 90.04 | 86 | 16.5 | 9.29 | 14.86 | 5.36 | 8.67 | 3505.74 | 1055.11 | 1355.72 | 776.54 | 8.88 | 1.62 | 4.36 | 63.41 | 680 | 5900 | 83.82 | 0.59 | 10.92 | 71.62 | 60 | 9 | 9 | 0.44 | 408 | 411.95 | 394940.4 | 274740.43 | 20230204-161315_9307c778-4377-450c-bcb6-c822eb934dd8 | 6.8607
22.38 | 31.65 | 5497.59 | 7.6 | [31.97, 42.17] | [25.38, 16.83] | [12.38, 12.38] | [6.74, 8.4] | 0 | 772.02 | 69.73 | 71.38 | -1.65 | 7.29 | 90.04 | 63 | 23.1 | 9.27 | 18.21 | 4.17 | 7.12 | 3518.46 | 1050.13 | 1270.68 | 756.05 | 8.3 | 1.63 | 4.33 | 68.96 | 680 | 5900 | 83.67 | 0.59 | 13.67 | 56.12 | 60 | 9 | 9 | 0.56 | 408 | 413.04 | 418683.02 | 339514.03 | 20230204-161315_74a80635-e644-4046-9984-5c01f8576e73 | 4.5188
21 | 30.2 | 5489.42 | 7.6 | [24.6, 46.53] | [24.99, 5.81] | [12.27, 12.27] | [6.48, 9.23] | 0 | 686.17 | 61.86 | 64.61 | -2.75 | 7.23 | 89.93 | 86 | 17.3 | 9.21 | 15.64 | 5.36 | 8 | 3513.23 | 1053.34 | 1318.04 | 767.61 | 6.7 | 1.62 | 4.36 | 63.23 | 680 | 5900 | 83.13 | 0.59 | 11.87 | 51.06 | 60 | 9 | 9 | 0.62 | 408 | 413.54 | 404538.1 | 216526.5 | 20230204-161315_e1290cce-948e-4477-b98c-ec25375053c9 | 10.7313
20.16 | 29.41 | 5452.2 | 7.6 | [23.85, 23.85] | [25.2, 25.2] | [12.3, 12.3] | [3.88, 3.88] | 0 | 673.19 | 61.35 | 61.35 | 0 | 7.22 | 90.07 | 77 | 17 | 9.25 | 14.3 | 5.86 | 8.1 | 3489.41 | 1046.87 | 1316.49 | 764.24 | 15.82 | 1.6 | 4.39 | 61.22 | 680 | 5900 | 83.52 | 0.59 | 11.77 | 121.52 | 60 | 9 | 9 | 0.26 | 408 | 410.33 | 380134.84 | 380134.84 | 20230204-161315_20fbdb18-33e5-4e31-bfe1-76df41a7e202 | 0
20.32 | 29.7 | 5498.98 | 7.6 | [20.57, 35.12] | [25.14, 15.57] | [12.29, 12.29] | [2.01, 7.0] | 0 | 624.95 | 58 | 62.98 | -4.98 | 7.19 | 89.99 | 86 | 16 | 9.39 | 14.37 | 5.95 | 8.8 | 3519.34 | 1059.16 | 1362.19 | 779.62 | 8.29 | 1.62 | 4.35 | 61.22 | 680 | 5900 | 84.72 | 0.59 | 10.86 | 67.34 | 60 | 9 | 9 | 0.47 | 408 | 412.2 | 357483.49 | 303633.34 | 20230204-161315_d2524044-50c0-471e-9160-5ca0a60c9f8e | 3.0736
22.34 | 31.6 | 5485.71 | 7.6 | [29.07, 55.0] | [24.61, 3.0] | [12.84, 12.84] | [6.58, 10.9] | 0 | 743.92 | 66.52 | 70.84 | -4.32 | 7.28 | 90.02 | 61 | 23 | 9.25 | 17.84 | 4.5 | 7.37 | 3510.85 | 1050.5 | 1291.54 | 761.05 | 6.1 | 1.64 | 4.32 | 67.28 | 680 | 5900 | 83.51 | 0.59 | 13.1 | 43.24 | 60 | 9 | 9 | 0.73 | 408 | 414.54 | 405408.33 | 206965.11 | 20230204-161315_6230373d-14ce-422d-8422-db746e92b142 | 11.3267
20.16 | 29.42 | 5528.05 | 7.6 | [16.55, 47.4] | [25.06, 1.11] | [12.51, 12.51] | [2.49, 9.39] | 0 | 556.5 | 54.12 | 61.02 | -6.9 | 7.15 | 89.97 | 84 | 16.8 | 9.25 | 14.92 | 5.24 | 9.93 | 3537.95 | 1071.07 | 1433.05 | 800.35 | 5.77 | 1.65 | 4.3 | 63.83 | 680 | 5900 | 83.52 | 0.59 | 9.35 | 50.2 | 60 | 9 | 9 | 0.63 | 408 | 413.63 | 358111.33 | 161527.11 | 20230204-161315_0ef14bcd-df90-453b-922f-49d6953fa13e | 11.2206
21.7 | 30.89 | 5536.4 | 7.6 | [22.67, 51.04] | [25.28, 2.3] | [12.39, 12.39] | [4.71, 10.11] | 0 | 654.87 | 60.34 | 65.73 | -5.39 | 7.21 | 89.93 | 73 | 21.2 | 9.19 | 17.79 | 3.92 | 8.45 | 3543.29 | 1064.33 | 1350.01 | 779.46 | 5.97 | 1.65 | 4.3 | 70.11 | 680 | 5900 | 82.92 | 0.59 | 11.12 | 46.6 | 60 | 9 | 9 | 0.67 | 408 | 414.07 | 388600.87 | 186563.33 | 20230204-161315_db37e0d8-9ac0-4cc2-b48e-c9dca0847f67 | 11.5318
20.21 | 29.4 | 5484.67 | 7.6 | [21.23, 24.96] | [24.56, 20.29] | [12.23, 12.23] | [5.54, 5.0] | 0 | 641.52 | 58.02 | 57.48 | 0.54 | 7.21 | 90.02 | 86 | 16.4 | 9.2 | 14.76 | 5.44 | 8.55 | 3510.19 | 1055.69 | 1349.7 | 775.51 | 11.61 | 1.62 | 4.36 | 62.82 | 680 | 5900 | 83.03 | 0.59 | 11 | 94.28 | 60 | 9 | 9 | 0.33 | 408 | 411 | 386752.6 | 332168.35 | 20230204-161315_07de088f-9dd3-4dda-97cf-d19eb18679a3 | 3.1155
20.54 | 29.71 | 5469.91 | 7.6 | [21.44, 25.79] | [25.37, 20.95] | [12.66, 12.66] | [5.24, 5.17] | 0 | 633.99 | 59.47 | 59.4 | 0.07 | 7.2 | 89.94 | 85 | 16.7 | 9.16 | 14.94 | 5.61 | 8.63 | 3500.74 | 1053.41 | 1351.84 | 774.92 | 11.51 | 1.63 | 4.35 | 62.05 | 680 | 5900 | 82.72 | 0.59 | 10.84 | 91.23 | 60 | 9 | 9 | 0.34 | 408 | 411.1 | 394234.39 | 343125.68 | 20230204-161315_47794b0e-b598-4ecd-8308-11c4a9b03d20 | 2.9172
20.93 | 30.15 | 5478.4 | 7.6 | [19.3, 50.44] | [24.95, 1.81] | [12.7, 12.7] | [2.0, 9.99] | 0 | 604.03 | 56.95 | 64.95 | -8 | 7.19 | 90 | 79 | 17.1 | 9.22 | 14.63 | 6.3 | 9.07 | 3506.18 | 1057.86 | 1381.39 | 783.43 | 5.7 | 1.65 | 4.31 | 59.42 | 680 | 5900 | 83.26 | 0.59 | 10.32 | 47.16 | 60 | 9 | 9 | 0.67 | 408 | 413.99 | 354375.71 | 179003.08 | 20230204-161315_d9e3c717-33a5-4af7-99f2-d8211b14a626 | 10.0099
20.74 | 29.97 | 5537.6 | 7.6 | [18.2, 47.81] | [24.85, 1.11] | [12.63, 12.63] | [3.59, 9.47] | 0 | 587 | 55.68 | 61.55 | -5.87 | 7.18 | 90.05 | 78 | 18.9 | 9.23 | 16.23 | 4.51 | 9.43 | 3544.06 | 1070.67 | 1410.75 | 795.59 | 5.88 | 1.66 | 4.29 | 67.19 | 680 | 5900 | 83.32 | 0.59 | 9.88 | 49.76 | 60 | 9 | 9 | 0.63 | 408 | 413.68 | 368337.6 | 162850.01 | 20230204-161315_4fac19bf-be0e-4830-b177-06b8b932ab9b | 11.7287
22.33 | 31.52 | 5488.39 | 7.6 | [26.63, 30.5] | [25.25, 21.47] | [12.07, 12.07] | [6.01, 6.1] | 0 | 711.71 | 63.95 | 64.04 | -0.09 | 7.25 | 90.05 | 63 | 22.9 | 9.19 | 18.03 | 4.3 | 7.71 | 3512.57 | 1051.11 | 1298.3 | 762.22 | 10.49 | 1.64 | 4.32 | 68.12 | 680 | 5900 | 82.95 | 0.59 | 12.36 | 77.27 | 60 | 9 | 9 | 0.41 | 408 | 411.66 | 404625.46 | 362597.96 | 20230204-161940_b5aa3c25-f98c-4548-a6bd-aefc752f69df | 2.3988
21.89 | 30.98 | 5468.69 | 7.59 | [11.61, 50.41] | [35.0, 2.95] | [11.57, 11.57] | [3.25, 9.99] | 0 | 388.07 | 58.18 | 64.93 | -6.75 | 6.94 | 89.96 | 89 | 20.2 | 9.09 | 18.84 | 3.05 | 14.09 | 3499.96 | 1063.16 | 1513.63 | 807.63 | 5.83 | 1.7 | 4.2 | 74.89 | 680 | 5900 | 82.09 | 0.59 | 6.27 | 47.18 | 60 | 9 | 9 | 0.67 | 408 | 413.99 | 482551.94 | 191949.55 | 20230204-161940_5215ea75-d554-4ddf-8c6c-29b51d7b9639 | 16.5869
21.98 | 31.09 | 5502.64 | 7.6 | [15.01, 20.27] | [25.52, 18.68] | [11.87, 11.87] | [5.66, 4.07] | 0 | 526.21 | 52.4 | 50.82 | 1.58 | 7.11 | 89.96 | 89 | 19.9 | 9.11 | 18.55 | 3.44 | 10.46 | 3521.69 | 1066.85 | 1440.91 | 799.31 | 12.89 | 1.68 | 4.23 | 72.6 | 680 | 5900 | 82.21 | 0.59 | 8.69 | 115.93 | 60 | 9 | 9 | 0.27 | 408 | 410.44 | 394007.76 | 298520.14 | 20230204-161940_669a4f16-6e26-47c3-bd3d-f0b3d1d0b95e | 5.4502
22.23 | 31.31 | 5495.65 | 7.6 | [25.8, 52.15] | [25.01, 3.26] | [11.77, 11.77] | [5.73, 10.34] | 0 | 705.3 | 62.58 | 67.18 | -4.6 | 7.24 | 89.98 | 83 | 20.8 | 9.09 | 18.68 | 3.55 | 7.79 | 3517.22 | 1052.55 | 1301.58 | 763.48 | 6.05 | 1.64 | 4.32 | 71.9 | 680 | 5900 | 82.02 | 0.59 | 12.08 | 45.6 | 60 | 9 | 9 | 0.69 | 408 | 414.2 | 397844.82 | 200943.03 | 20230204-161940_1696e315-f61f-4157-9758-68c416da3ba7 | 11.2387
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.71 | 30.85 | 5481.31 | 7.6 | [8.47, 47.47] | [34.93, 1.74] | [11.91, 11.91] | [3.59, 9.4] | 0 | 322.58 | 55.31 | 61.12 | -5.81 | 6.9 | 89.72 | 94 | 19.5 | 9.13 | 18.77 | 2.95 | 16.99 | 3508.04 | 1077.29 | 1649.02 | 841.76 | 5.88 | 1.75 | 4.11 | 75.61 | 680 | 5900 | 82.45 | 0.59 | 5.16 | 50.11 | 60 | 9 | 9 | 0.63 | 408 | 413.64 | 482647.36 | 168957 | 20230204-161940_8298a46e-ef95-4a25-9f54-4b055c90b1fd | 17.9047
22.03 | 31.17 | 5504.76 | 7.6 | [24.27, 27.54] | [25.0, 21.52] | [11.58, 11.58] | [5.72, 5.51] | 0 | 685.81 | 60.85 | 60.64 | 0.21 | 7.22 | 89.85 | 84 | 20.7 | 9.14 | 18.71 | 3.32 | 8.03 | 3523.05 | 1055.07 | 1313 | 766.94 | 11.04 | 1.64 | 4.32 | 73.34 | 680 | 5900 | 82.49 | 0.59 | 11.74 | 85.49 | 60 | 9 | 9 | 0.37 | 408 | 411.31 | 396139.28 | 354245.22 | 20230204-161940_a2738943-0b03-446e-b973-af40f204db84 | 2.3912
21.32 | 30.5 | 5472.67 | 7.59 | [8.98, 49.05] | [35.01, 2.65] | [11.48, 11.48] | [2.0, 9.72] | 0 | 333.42 | 55.47 | 63.18 | -7.71 | 6.89 | 89.95 | 97 | 17.7 | 9.17 | 17.34 | 3.99 | 16.41 | 3502.51 | 1071.59 | 1608.29 | 830.14 | 5.71 | 1.71 | 4.16 | 69.71 | 680 | 5900 | 82.82 | 0.59 | 5.37 | 48.48 | 60 | 9 | 9 | 0.65 | 408 | 413.83 | 467546.43 | 184284.13 | 20230204-161940_f5f80809-4d1f-4fc5-b958-c04a0e03ef20 | 16.1679
22.34 | 31.49 | 5491.35 | 7.6 | [26.88, 41.72] | [25.1, 12.81] | [11.85, 11.85] | [5.75, 8.3] | 0 | 717.97 | 63.83 | 66.38 | -2.55 | 7.25 | 89.97 | 77 | 21.2 | 9.15 | 18.3 | 4.05 | 7.65 | 3514.46 | 1051.09 | 1293.64 | 761.15 | 7.69 | 1.64 | 4.32 | 69.33 | 680 | 5900 | 82.55 | 0.59 | 12.42 | 56.8 | 60 | 9 | 9 | 0.55 | 408 | 412.98 | 400161.21 | 288262.77 | 20230204-161940_71363234-a300-4312-9579-39e8b34096b7 | 6.3869
22.34 | 31.61 | 5490.96 | 7.6 | [25.98, 52.47] | [25.06, 2.76] | [12.35, 12.35] | [6.2, 10.4] | 0 | 703.46 | 63.39 | 67.58 | -4.19 | 7.25 | 89.95 | 61 | 23 | 9.27 | 17.84 | 4.49 | 7.81 | 3514.22 | 1052.68 | 1308.23 | 765.25 | 6.1 | 1.64 | 4.31 | 67.37 | 680 | 5900 | 83.72 | 0.59 | 12.3 | 45.32 | 60 | 9 | 9 | 0.69 | 408 | 414.24 | 403905.38 | 196313.24 | 20230204-161940_55fd6eec-b5c6-42ff-94f0-3f6212519031 | 11.8489
22.3 | 31.49 | 5492.31 | 7.6 | [25.46, 33.22] | [24.67, 17.71] | [12.02, 12.02] | [5.83, 6.63] | 0 | 702.81 | 62.15 | 62.95 | -0.8 | 7.24 | 90 | 66 | 22.6 | 9.19 | 18.16 | 4.13 | 7.81 | 3515.08 | 1052.76 | 1307.36 | 765.03 | 9.38 | 1.65 | 4.31 | 68.98 | 680 | 5900 | 82.95 | 0.59 | 12.17 | 71.11 | 60 | 9 | 9 | 0.44 | 408 | 411.98 | 394559.57 | 324185.26 | 20230204-161940_7f7d2fa2-4db7-4bfc-a70a-bf94d004b1c4 | 4.0168
22.29 | 31.35 | 5476.92 | 7.6 | [22.22, 49.54] | [25.2, 2.16] | [12.1, 12.1] | [5.54, 9.81] | 0 | 650.79 | 59.52 | 63.8 | -4.28 | 7.21 | 90.04 | 84 | 20.9 | 9.06 | 18.9 | 3.39 | 8.42 | 3505.23 | 1052.69 | 1334.88 | 770.7 | 6.06 | 1.66 | 4.29 | 72.78 | 680 | 5900 | 81.79 | 0.59 | 11.03 | 48.02 | 60 | 9 | 9 | 0.65 | 408 | 413.89 | 395331.07 | 180184.76 | 20230204-161940_6bb85cae-d577-4efa-9e80-71e64d32fdac | 12.28
22.08 | 31.13 | 5451.56 | 7.62 | [5.9, 46.03] | [34.98, 1.36] | [11.88, 11.88] | [2.61, 9.12] | 0 | 262.95 | 52.76 | 59.27 | -6.51 | 6.85 | 90.13 | 91 | 19.6 | 9.05 | 18.5 | 3.58 | 20.73 | 3489 | 1085.01 | 1801.44 | 875.54 | 5.79 | 1.81 | 4 | 71.64 | 680 | 5900 | 81.7 | 0.59 | 4.14 | 51.68 | 60 | 9 | 9 | 0.61 | 408 | 413.47 | 471153.24 | 160062.62 | 20230204-161940_330582db-8de1-4789-af78-f5c23e0515fd | 17.7563
22.33 | 31.59 | 5486.02 | 7.6 | [25.44, 52.22] | [25.28, 2.49] | [12.54, 12.54] | [6.36, 10.35] | 0 | 692.8 | 63.26 | 67.25 | -3.99 | 7.24 | 90.1 | 62 | 23.3 | 9.26 | 18.25 | 4.08 | 7.92 | 3511.05 | 1052.51 | 1314.68 | 766.58 | 6.11 | 1.65 | 4.31 | 69.43 | 680 | 5900 | 83.56 | 0.59 | 12.08 | 45.55 | 60 | 9 | 9 | 0.69 | 408 | 414.21 | 407930.09 | 192361.5 | 20230204-161940_4e8d8934-b950-42ab-91de-02eab0731f3f | 12.3041
22.19 | 31.25 | 5512.16 | 7.6 | [20.65, 47.32] | [25.01, 1.9] | [11.72, 11.72] | [5.81, 9.38] | 0 | 630.76 | 57.38 | 60.94 | -3.56 | 7.19 | 89.91 | 84 | 20.5 | 9.06 | 18.51 | 3.68 | 8.74 | 3527.78 | 1060.25 | 1353.6 | 777.97 | 6.12 | 1.65 | 4.29 | 71.14 | 680 | 5900 | 81.79 | 0.59 | 10.57 | 50.26 | 60 | 9 | 9 | 0.63 | 408 | 413.63 | 394111.11 | 170236.89 | 20230204-161940_49b0d643-eca4-4310-95e9-df8668edea2c | 12.7782
22.09 | 31.17 | 5502.13 | 7.6 | [17.37, 44.43] | [24.89, 0.96] | [11.81, 11.81] | [5.67, 8.8] | 0 | 576.36 | 54.07 | 57.2 | -3.13 | 7.15 | 90.23 | 89 | 19.4 | 9.08 | 18.06 | 4.03 | 9.55 | 3521.36 | 1062.8 | 1397.17 | 788.44 | 6.14 | 1.67 | 4.26 | 69.24 | 680 | 5900 | 81.95 | 0.59 | 9.59 | 53.55 | 60 | 9 | 9 | 0.59 | 408 | 413.28 | 388396.51 | 150414.79 | 20230204-161940_b8b608f7-a603-484a-8c2a-a4d159c353b0 | 13.5834
21.89 | 31 | 5473.76 | 7.6 | [9.6, 50.26] | [35.06, 2.35] | [12.12, 12.12] | [2.0, 9.96] | 0 | 345.92 | 56.78 | 64.73 | -7.95 | 6.92 | 90.01 | 92 | 19.1 | 9.1 | 18.13 | 3.76 | 15.82 | 3503.21 | 1072.31 | 1602.56 | 830.43 | 5.7 | 1.73 | 4.13 | 70.75 | 680 | 5900 | 82.19 | 0.59 | 5.54 | 47.32 | 60 | 9 | 9 | 0.66 | 408 | 413.97 | 469317.51 | 184684.01 | 20230204-161940_b098edc8-b0f1-4c75-a2af-7f67c5b1a006 | 16.2462
21.11 | 30.26 | 5471.34 | 7.61 | [9.5, 48.38] | [33.47, 2.18] | [11.74, 11.74] | [2.0, 9.58] | 0 | 353.18 | 54.71 | 62.3 | -7.59 | 6.93 | 89.99 | 97 | 17.3 | 9.15 | 16.94 | 4.18 | 15.49 | 3501.66 | 1071.37 | 1593.12 | 828.4 | 5.71 | 1.72 | 4.16 | 68.66 | 680 | 5900 | 82.58 | 0.59 | 5.7 | 49.17 | 60 | 9 | 9 | 0.64 | 408 | 413.75 | 449433.6 | 176814.41 | 20230204-161940_78126632-cfb1-4c76-bca9-725a05622f37 | 15.5605
22.27 | 31.33 | 5473.76 | 7.6 | [13.5, 50.88] | [34.88, 2.4] | [12.25, 12.25] | [5.19, 10.08] | 0 | 423.64 | 60.63 | 65.53 | -4.9 | 6.98 | 90.26 | 83 | 20.6 | 9.06 | 18.48 | 3.79 | 12.92 | 3503.21 | 1062.25 | 1481.89 | 801.89 | 6.01 | 1.7 | 4.2 | 70.51 | 680 | 5900 | 81.8 | 0.59 | 6.86 | 46.75 | 60 | 9 | 9 | 0.67 | 408 | 414.05 | 503040.77 | 187129.04 | 20230204-161940_d0654960-d4a8-4ebf-89e8-4ef79766dafd | 18.0315
21.97 | 31.05 | 5468.28 | 7.59 | [7.67, 47.83] | [35.0, 2.32] | [11.45, 11.45] | [2.0, 9.48] | 0 | 304.35 | 54.12 | 61.6 | -7.48 | 6.87 | 90.03 | 95 | 18.6 | 9.07 | 17.99 | 3.98 | 17.97 | 3499.7 | 1076.02 | 1671.14 | 844.56 | 5.71 | 1.74 | 4.1 | 69.51 | 680 | 5900 | 81.91 | 0.59 | 4.83 | 49.73 | 60 | 9 | 9 | 0.63 | 408 | 413.69 | 466297.43 | 176690.37 | 20230204-161940_24999d64-ae9a-4bf1-9e01-545f40a200af | 16.5301
21.96 | 31.1 | 5468.71 | 7.61 | [9.21, 48.88] | [34.95, 2.97] | [11.11, 11.11] | [2.0, 9.69] | 0 | 339.04 | 55.27 | 62.96 | -7.69 | 6.89 | 89.95 | 90 | 19.4 | 9.14 | 18.18 | 3.78 | 16.13 | 3499.97 | 1068.38 | 1584.95 | 823.38 | 5.71 | 1.74 | 4.14 | 70.73 | 680 | 5900 | 82.47 | 0.59 | 5.45 | 48.65 | 60 | 9 | 9 | 0.65 | 408 | 413.81 | 466804.61 | 187391.04 | 20230204-161940_55dd3712-5842-40af-bdac-f0237564dada | 15.9483
21.73 | 30.86 | 5464.02 | 7.61 | [6.83, 47.29] | [35.0, 1.9] | [11.71, 11.71] | [2.0, 9.37] | 0 | 284.94 | 53.54 | 60.9 | -7.36 | 6.86 | 90.01 | 96 | 18.1 | 9.14 | 17.62 | 4.11 | 19.18 | 3496.97 | 1080.78 | 1730.54 | 859.1 | 5.71 | 1.77 | 4.06 | 68.97 | 680 | 5900 | 82.48 | 0.59 | 4.54 | 50.29 | 60 | 9 | 9 | 0.62 | 408 | 413.62 | 465877.27 | 170226.55 | 20230204-161940_7f6e81ff-6745-494e-aae9-8fb1819f0153 | 16.875
22.19 | 31.21 | 5453.04 | 7.6 | [7.36, 44.62] | [34.93, 1.94] | [10.91, 10.91] | [4.58, 8.84] | 0 | 297.58 | 53.2 | 57.47 | -4.27 | 6.86 | 90.09 | 88 | 20.1 | 9.02 | 18.62 | 3.57 | 18.32 | 3489.95 | 1071.78 | 1664.07 | 840.01 | 6.02 | 1.75 | 4.09 | 71.66 | 680 | 5900 | 81.45 | 0.59 | 4.7 | 53.31 | 60 | 9 | 9 | 0.59 | 408 | 413.3 | 491014.62 | 162201.25 | 20230204-161940_b6524f31-8bbc-4434-a8eb-a220a1e50913 | 18.7679
22.05 | 31.15 | 5458.09 | 7.58 | [6.59, 46.82] | [34.98, 1.99] | [11.49, 11.49] | [2.04, 9.28] | 0 | 279.25 | 53.06 | 60.3 | -7.24 | 6.85 | 89.95 | 90 | 19.6 | 9.1 | 18.38 | 3.68 | 19.55 | 3493.18 | 1079.84 | 1736.77 | 859.4 | 5.72 | 1.75 | 4.07 | 71.2 | 680 | 5900 | 82.11 | 0.59 | 4.43 | 50.8 | 60 | 9 | 9 | 0.62 | 408 | 413.57 | 465621.83 | 169703.19 | 20230204-161940_f791e109-5949-460c-9ee6-75d59a50a7f3 | 16.8903
22.37 | 31.59 | 5496.87 | 7.6 | [29.02, 35.11] | [24.7, 19.51] | [11.94, 11.94] | [6.11, 7.01] | 0 | 748.35 | 65.66 | 66.56 | -0.9 | 7.27 | 89.96 | 62 | 22.9 | 9.22 | 17.89 | 4.48 | 7.35 | 3517.99 | 1051 | 1281.56 | 758.71 | 9.37 | 1.64 | 4.33 | 67.32 | 680 | 5900 | 83.26 | 0.59 | 13.12 | 67.26 | 60 | 9 | 9 | 0.47 | 408 | 412.2 | 400971.31 | 351665.4 | 20230204-161940_16b7d7f2-6364-44cd-b718-af28e797449f | 2.8143
22.17 | 31.15 | 5483.9 | 7.6 | [19.06, 42.25] | [25.0, 4.49] | [11.91, 11.91] | [5.71, 8.38] | 0 | 603.95 | 55.97 | 58.65 | -2.68 | 7.17 | 90.12 | 90 | 19.8 | 8.98 | 18.57 | 3.6 | 9.08 | 3509.7 | 1057.17 | 1370.09 | 780.14 | 6.68 | 1.67 | 4.27 | 71.4 | 680 | 5900 | 81.04 | 0.59 | 10.03 | 56.25 | 60 | 9 | 9 | 0.56 | 408 | 413.03 | 391700.17 | 187592.72 | 20230204-161940_011fb6e1-ac91-412d-8071-8965b7627169 | 11.65
20.96 | 30.06 | 5474.18 | 7.6 | [16.3, 46.91] | [25.04, 1.72] | [11.77, 11.77] | [2.0, 9.29] | 0 | 555.69 | 53.11 | 60.4 | -7.29 | 7.14 | 89.84 | 97 | 16.9 | 9.1 | 16.54 | 4.42 | 9.85 | 3503.48 | 1058.91 | 1406.81 | 788.56 | 5.72 | 1.65 | 4.29 | 67.29 | 680 | 5900 | 82.17 | 0.59 | 9.28 | 50.71 | 60 | 9 | 9 | 0.62 | 408 | 413.58 | 351976.51 | 166959.94 | 20230204-162602_6cb08677-e976-45ae-87db-f4548b79c838 | 10.5603
22.67 | 31.66 | 5504.84 | 7.59 | [25.85, 32.58] | [24.69, 17.5] | [11.66, 11.66] | [6.96, 6.5] | 0 | 710.11 | 62.2 | 61.74 | 0.46 | 7.24 | 89.97 | 86 | 21 | 8.99 | 19.25 | 3.42 | 7.75 | 3523.1 | 1054.12 | 1301.48 | 764.21 | 9.57 | 1.64 | 4.31 | 72.46 | 680 | 5900 | 81.16 | 0.59 | 12.02 | 72.5 | 60 | 9 | 9 | 0.43 | 408 | 411.9 | 406357.86 | 319483.46 | 20230204-162602_f75dbaf7-3d38-45a0-93cd-f27506314615 | 4.9586
22.66 | 31.64 | 5522.17 | 7.6 | [23.27, 49.03] | [24.79, 2.43] | [11.69, 11.69] | [6.32, 9.72] | 0 | 672.95 | 59.75 | 63.15 | -3.4 | 7.22 | 90.01 | 84 | 21.3 | 8.98 | 19.29 | 3.37 | 8.21 | 3534.19 | 1059.56 | 1328.01 | 772.31 | 6.15 | 1.66 | 4.28 | 72.7 | 680 | 5900 | 81.08 | 0.59 | 11.25 | 48.51 | 60 | 9 | 9 | 0.65 | 408 | 413.83 | 398906.9 | 181694.8 | 20230204-162602_db6e0a5f-c355-4cd8-8129-4f8633a2f92e | 12.398
20.64 | 29.73 | 5498.7 | 7.6 | [14.95, 45.74] | [25.24, 1.5] | [11.65, 11.65] | [2.0, 9.06] | 0 | 528.57 | 51.84 | 58.89 | -7.05 | 7.11 | 90.06 | 98 | 16.7 | 9.09 | 16.45 | 4.19 | 10.4 | 3519.17 | 1065.62 | 1435.71 | 797.57 | 5.72 | 1.66 | 4.28 | 68.46 | 680 | 5900 | 82.05 | 0.59 | 8.73 | 52.01 | 60 | 9 | 9 | 0.6 | 408 | 413.44 | 353154.3 | 160784.68 | 20230204-162602_a0537208-1951-4fe6-b9d7-d3f77f3698b1 | 10.98
21.27 | 30.33 | 5470.03 | 7.61 | [14.49, 18.65] | [24.99, 22.58] | [11.36, 11.36] | [2.0, 3.76] | 0 | 523.05 | 50.84 | 52.59 | -1.75 | 7.11 | 90.04 | 98 | 17.1 | 9.05 | 16.85 | 4.42 | 10.46 | 3500.82 | 1060.1 | 1430.27 | 793.68 | 13.53 | 1.67 | 4.26 | 67.19 | 680 | 5900 | 81.7 | 0.59 | 8.64 | 125.43 | 60 | 9 | 9 | 0.25 | 408 | 410.25 | 349463.94 | 341424.34 | 20230204-162602_1ad30b17-4fbc-4f3e-a995-e7e0ad0ce9a1 | 0.45888
20.83 | 29.89 | 5517.46 | 7.6 | [18.46, 48.67] | [25.32, 2.24] | [11.77, 11.77] | [2.51, 9.64] | 0 | 591.22 | 55.55 | 62.68 | -7.13 | 7.16 | 90.01 | 97 | 16.8 | 9.06 | 16.44 | 4.4 | 9.33 | 3531.18 | 1063.98 | 1384.17 | 786.06 | 5.76 | 1.64 | 4.31 | 67.32 | 680 | 5900 | 81.79 | 0.59 | 9.82 | 48.86 | 60 | 9 | 9 | 0.64 | 408 | 413.79 | 362504.58 | 178415.74 | 20230204-162602_35725284-e655-4bdd-9c7f-64255cac374b | 10.5074
22.71 | 31.73 | 5513.95 | 7.6 | [21.51, 47.37] | [25.04, 1.97] | [11.67, 11.67] | [6.6, 9.38] | 0 | 644.22 | 58.22 | 61.01 | -2.79 | 7.19 | 90.04 | 85 | 21 | 9.02 | 19.12 | 3.59 | 8.56 | 3528.93 | 1059.54 | 1343.37 | 775.44 | 6.2 | 1.67 | 4.27 | 71.55 | 680 | 5900 | 81.45 | 0.59 | 10.78 | 50.21 | 60 | 9 | 9 | 0.63 | 408 | 413.63 | 403274.74 | 171187.7 | 20230204-162602_6402f738-41ad-49a3-925b-08f6a2748f4a | 13.247
20.9 | 30 | 5488.11 | 7.6 | [18.78, 18.78] | [25.29, 25.29] | [11.73, 11.73] | [2.0, 2.0] | 0 | 597.19 | 55.8 | 55.8 | 0 | 7.16 | 89.95 | 98 | 16.8 | 9.1 | 16.55 | 4.35 | 9.19 | 3512.39 | 1057.8 | 1371.49 | 780.5 | 27.92 | 1.64 | 4.32 | 67.67 | 680 | 5900 | 82.12 | 0.59 | 10.03 | 235.82 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 357213.32 | 357213.32 | 20230204-162602_8f298c37-cf64-402d-94f8-78d928747063 | 0
20.83 | 29.86 | 5519.12 | 7.6 | [16.96, 42.46] | [24.64, 4.77] | [11.71, 11.71] | [2.79, 8.42] | 0 | 571.98 | 53.31 | 58.94 | -5.63 | 7.15 | 90.03 | 97 | 16.9 | 9.04 | 16.54 | 4.29 | 9.65 | 3532.24 | 1066.48 | 1405.6 | 791.93 | 6.33 | 1.65 | 4.3 | 67.8 | 680 | 5900 | 81.58 | 0.59 | 9.43 | 55.97 | 60 | 9 | 9 | 0.56 | 408 | 413.05 | 355656.81 | 191551.34 | 20230204-162602_6ee43f9d-1c3f-490d-a050-08ec37dfcaeb | 9.3668
22.42 | 31.42 | 5532.29 | 7.6 | [23.58, 39.37] | [25.33, 11.46] | [11.79, 11.79] | [5.9, 7.83] | 0 | 671.09 | 60.7 | 62.62 | -1.92 | 7.21 | 89.96 | 85 | 21 | 9.01 | 19.12 | 3.29 | 8.24 | 3540.67 | 1061.35 | 1329.71 | 773.41 | 7.75 | 1.66 | 4.28 | 73.22 | 680 | 5900 | 81.29 | 0.59 | 11.22 | 60.2 | 60 | 9 | 9 | 0.52 | 408 | 412.7 | 401559.37 | 264855.77 | 20230204-162602_90ef631e-a868-43ff-9ee3-a9d271025600 | 7.8027
22.82 | 31.89 | 5471.23 | 7.6 | [25.17, 39.71] | [25.0, 12.05] | [11.41, 11.41] | [6.3, 7.9] | 0 | 699.23 | 61.58 | 63.17 | -1.59 | 7.23 | 90.04 | 80 | 22 | 9.06 | 19.45 | 3.37 | 7.82 | 3501.58 | 1047.61 | 1294.94 | 759.58 | 7.8 | 1.65 | 4.3 | 72.87 | 680 | 5900 | 81.8 | 0.59 | 11.99 | 59.67 | 60 | 9 | 9 | 0.53 | 408 | 412.74 | 402674.69 | 272792.57 | 20230204-162602_99045306-03a0-4762-9b7c-0c8277dbc925 | 7.4134
21.85 | 30.92 | 5542.5 | 7.6 | [22.31, 39.09] | [25.34, 11.48] | [11.61, 11.61] | [4.86, 7.77] | 0 | 653.6 | 59.26 | 62.18 | -2.92 | 7.2 | 89.97 | 90 | 19.7 | 9.07 | 18.47 | 3.38 | 8.48 | 3547.2 | 1064.03 | 1341.04 | 776.91 | 7.62 | 1.65 | 4.3 | 72.84 | 680 | 5900 | 81.86 | 0.59 | 10.94 | 60.64 | 60 | 9 | 9 | 0.52 | 408 | 412.66 | 389794.57 | 264154.8 | 20230204-162602_f6a6d0fb-a0f1-4555-93d1-4688dd52685a | 7.1712
22.14 | 31.17 | 5532.99 | 7.6 | [22.25, 35.63] | [24.64, 12.92] | [11.72, 11.72] | [5.42, 7.09] | 0 | 659.36 | 58.61 | 60.27 | -1.66 | 7.21 | 90 | 85 | 20.5 | 9.03 | 18.64 | 3.5 | 8.39 | 3541.11 | 1062.7 | 1341.11 | 776.6 | 8.26 | 1.66 | 4.29 | 72.04 | 680 | 5900 | 81.49 | 0.59 | 11.03 | 66.45 | 60 | 9 | 9 | 0.47 | 408 | 412.26 | 387051.13 | 272038.14 | 20230204-162602_55c4c123-e1f6-47b3-9608-d1900a8c47f8 | 6.5647
20.87 | 29.93 | 5514.37 | 7.6 | [18.31, 48.24] | [24.8, 2.17] | [11.71, 11.71] | [2.26, 9.56] | 0 | 594.35 | 54.82 | 62.12 | -7.3 | 7.16 | 89.93 | 96 | 17.1 | 9.06 | 16.62 | 4.25 | 9.28 | 3529.2 | 1063.56 | 1383.89 | 785.95 | 5.74 | 1.64 | 4.31 | 68.06 | 680 | 5900 | 81.81 | 0.59 | 9.88 | 49.31 | 60 | 9 | 9 | 0.64 | 408 | 413.73 | 353352.01 | 176268.89 | 20230204-162602_8be5066a-76cd-4808-9a0c-89cdb3de2d8a | 10.1075
22.82 | 31.82 | 5488.64 | 7.6 | [27.46, 31.72] | [24.73, 20.0] | [11.64, 11.64] | [6.81, 6.34] | 0 | 730.79 | 63.83 | 63.36 | 0.47 | 7.26 | 89.87 | 79 | 22 | 9 | 19.32 | 3.5 | 7.51 | 3512.73 | 1049.85 | 1285.57 | 758.86 | 10.07 | 1.65 | 4.31 | 71.99 | 680 | 5900 | 81.25 | 0.59 | 12.48 | 74.37 | 60 | 9 | 9 | 0.42 | 408 | 411.8 | 406762.7 | 347658.12 | 20230204-162602_68e631f7-fe63-4606-be36-47dc9a792f90 | 3.3735
22.58 | 31.61 | 5514.15 | 7.6 | [24.64, 50.11] | [25.14, 2.8] | [11.63, 11.63] | [6.8, 9.93] | 0 | 688.97 | 61.41 | 64.54 | -3.13 | 7.22 | 89.92 | 89 | 20.4 | 9.03 | 19.04 | 3.54 | 8 | 3529.05 | 1056.67 | 1313.13 | 767.7 | 6.18 | 1.65 | 4.29 | 71.83 | 680 | 5900 | 81.54 | 0.59 | 11.64 | 47.46 | 60 | 9 | 9 | 0.66 | 408 | 413.96 | 409248.16 | 189337.21 | 20230204-162602_432aac77-3e85-4667-84ed-4536c19bc1a3 | 12.552
20.82 | 29.87 | 5509.81 | 7.6 | [14.73, 45.19] | [24.99, 1.4] | [11.6, 11.6] | [2.08, 8.95] | 0 | 526.95 | 51.32 | 58.19 | -6.87 | 7.11 | 89.99 | 97 | 17.1 | 9.05 | 16.74 | 4.09 | 10.46 | 3526.28 | 1068.1 | 1441.53 | 800 | 5.73 | 1.67 | 4.27 | 68.87 | 680 | 5900 | 81.65 | 0.59 | 8.63 | 52.64 | 60 | 9 | 9 | 0.6 | 408 | 413.37 | 350605.83 | 157890.39 | 20230204-162602_df9e1869-b550-4c2b-8981-f7679fbcbf21 | 10.9997
21.7 | 30.74 | 5544.17 | 7.6 | [19.86, 47.64] | [24.64, 2.08] | [11.63, 11.63] | [4.22, 9.44] | 0 | 622.32 | 56.13 | 61.35 | -5.22 | 7.18 | 89.93 | 95 | 18.7 | 9.04 | 18.09 | 3.6 | 8.91 | 3548.27 | 1067.18 | 1369.01 | 784.49 | 5.95 | 1.66 | 4.29 | 71.51 | 680 | 5900 | 81.64 | 0.59 | 10.32 | 49.93 | 60 | 9 | 9 | 0.63 | 408 | 413.66 | 372672.04 | 173344.54 | 20230204-162602_ebe99646-f5e2-422b-98da-f07c1bd2b4c9 | 11.3771
21.44 | 30.41 | 5539.94 | 7.6 | [16.06, 38.23] | [25.18, 7.03] | [11.66, 11.66] | [3.57, 7.59] | 0 | 550.32 | 52.9 | 56.92 | -4.02 | 7.13 | 89.93 | 97 | 18.1 | 8.96 | 17.74 | 3.7 | 10.07 | 3545.56 | 1071.67 | 1425.58 | 798.3 | 6.97 | 1.67 | 4.26 | 70.76 | 680 | 5900 | 80.92 | 0.59 | 8.93 | 62.09 | 60 | 9 | 9 | 0.51 | 408 | 412.55 | 369414.85 | 207002.65 | 20230204-162602_f7f0ce25-407c-4b30-968e-a967772b3d1d | 9.2701
20.73 | 29.84 | 5496.42 | 7.6 | [17.39, 43.5] | [24.71, 5.23] | [11.66, 11.66] | [2.0, 8.63] | 0 | 579.24 | 53.76 | 60.39 | -6.63 | 7.15 | 90.02 | 98 | 16.6 | 9.11 | 16.35 | 4.38 | 9.49 | 3517.71 | 1061.3 | 1392.02 | 786.6 | 6.23 | 1.65 | 4.31 | 67.54 | 680 | 5900 | 82.23 | 0.59 | 9.69 | 54.62 | 60 | 9 | 9 | 0.58 | 408 | 413.18 | 348854.68 | 200164.35 | 20230204-162602_59b604ee-f80e-429e-9f33-a8d2fe874ab9 | 8.4869
22.82 | 31.86 | 5485.37 | 7.6 | [28.51, 39.17] | [25.0, 15.51] | [11.61, 11.61] | [6.63, 7.8] | 0 | 741.1 | 65.12 | 66.29 | -1.17 | 7.26 | 90.02 | 80 | 22 | 9.04 | 19.45 | 3.37 | 7.4 | 3510.63 | 1048.46 | 1277.54 | 756.44 | 8.35 | 1.64 | 4.31 | 72.85 | 680 | 5900 | 81.59 | 0.59 | 12.75 | 60.42 | 60 | 9 | 9 | 0.52 | 408 | 412.68 | 409090.43 | 313962.36 | 20230204-162602_80f6217c-e0f0-4c1a-b291-b25f8547d817 | 5.4297
21.08 | 30.2 | 5485.55 | 7.59 | [16.2, 36.6] | [25.0, 9.88] | [11.71, 11.71] | [2.0, 7.27] | 0 | 554.43 | 52.91 | 58.19 | -5.28 | 7.14 | 89.97 | 98 | 17.1 | 9.11 | 16.85 | 4.23 | 9.89 | 3510.75 | 1061.11 | 1410.13 | 790.25 | 7.28 | 1.65 | 4.29 | 68.3 | 680 | 5900 | 82.27 | 0.59 | 9.25 | 64.79 | 60 | 9 | 9 | 0.48 | 408 | 412.36 | 351451.24 | 237408.24 | 20230204-162602_b4176341-9e94-4677-8a3b-64dc122428ec | 6.5093
21.03 | 30.03 | 5522.59 | 7.6 | [14.11, 44.05] | [25.17, 0.92] | [11.74, 11.74] | [3.04, 8.72] | 0 | 512.32 | 51.02 | 56.71 | -5.69 | 7.11 | 90.06 | 97 | 17.3 | 9 | 16.94 | 4.1 | 10.78 | 3534.46 | 1072.24 | 1461.89 | 806.27 | 5.85 | 1.68 | 4.25 | 68.73 | 680 | 5900 | 81.27 | 0.59 | 8.31 | 54.01 | 60 | 9 | 9 | 0.58 | 408 | 413.23 | 362140.16 | 148772.32 | 20230204-162602_99be4bf4-0735-420d-b4ff-792e3783208c | 12.1785
22.79 | 31.87 | 5475.06 | 7.6 | [26.16, 38.27] | [24.98, 14.6] | [11.89, 11.89] | [5.89, 7.62] | 0 | 709.59 | 63.03 | 64.76 | -1.73 | 7.24 | 89.99 | 78 | 22 | 9.08 | 19.19 | 3.6 | 7.72 | 3504.04 | 1048.59 | 1295.75 | 760.48 | 8.27 | 1.65 | 4.3 | 71.62 | 680 | 5900 | 81.95 | 0.59 | 12.2 | 61.86 | 60 | 9 | 9 | 0.51 | 408 | 412.57 | 399598.52 | 300347.06 | 20230204-162602_1682a359-b710-4c8c-b165-638bbb24d498 | 5.665
20.99 | 30.01 | 5482.14 | 7.6 | [17.56, 47.99] | [25.01, 2.08] | [11.73, 11.73] | [2.0, 9.51] | 0 | 578.95 | 54.3 | 61.8 | -7.5 | 7.15 | 90.01 | 98 | 17 | 9.03 | 16.75 | 4.23 | 9.47 | 3508.57 | 1058.4 | 1387.49 | 784.25 | 5.71 | 1.65 | 4.3 | 68.07 | 680 | 5900 | 81.48 | 0.59 | 9.62 | 49.56 | 60 | 9 | 9 | 0.63 | 408 | 413.71 | 352636.4 | 174445.1 | 20230204-162602_8e4c90e8-c938-4dbc-85f2-1b8b57d6a6ed | 10.1707
22.75 | 31.76 | 5496.02 | 7.6 | [22.58, 27.79] | [25.25, 18.65] | [11.88, 11.88] | [6.95, 5.55] | 0 | 656.86 | 59.71 | 58.32 | 1.39 | 7.21 | 90.08 | 85 | 20.8 | 9.01 | 18.93 | 3.82 | 8.37 | 3517.46 | 1055.5 | 1331.98 | 771.24 | 10.75 | 1.67 | 4.27 | 70.22 | 680 | 5900 | 81.37 | 0.59 | 11.04 | 84.85 | 60 | 9 | 9 | 0.37 | 408 | 411.33 | 410450.37 | 319925.46 | 20230204-162602_4e869081-fd05-470c-99e3-3f4cf39634b1 | 5.1669
22.53 | 31.47 | 5512.53 | 7.59 | [14.57, 39.57] | [25.42, 2.53] | [12.8, 12.8] | [5.73, 7.84] | 0 | 514.75 | 52.79 | 54.9 | -2.11 | 7.13 | 90.09 | 96 | 19.5 | 8.94 | 19.01 | 3.52 | 10.71 | 3528.02 | 1072.62 | 1475.36 | 810.15 | 6.73 | 1.7 | 4.19 | 71.77 | 680 | 5900 | 80.67 | 0.59 | 8.31 | 60.09 | 60 | 9 | 9 | 0.52 | 408 | 412.71 | 393884.6 | 156573.7 | 20230204-163228_9cadf07f-d77d-4cf3-9589-b1c2fd0c30fa | 13.5451
22.25 | 31.35 | 5486.37 | 7.6 | [21.72, 28.88] | [24.99, 19.89] | [11.85, 11.85] | [3.71, 5.77] | 0 | 646.87 | 58.56 | 60.62 | -2.06 | 7.2 | 90.03 | 85 | 20.4 | 9.09 | 18.54 | 3.71 | 8.48 | 3511.28 | 1054.49 | 1337.89 | 772.08 | 10.14 | 1.65 | 4.29 | 71 | 680 | 5900 | 82.08 | 0.59 | 10.97 | 81.62 | 60 | 9 | 9 | 0.38 | 408 | 411.46 | 373579.61 | 338288.99 | 20230204-163228_d4aac477-4f9f-441e-9337-757c6a96df4a | 2.0143
22.35 | 31.44 | 5475.96 | 7.6 | [23.86, 28.1] | [24.99, 22.1] | [11.68, 11.68] | [4.27, 5.63] | 0 | 679.42 | 60.53 | 61.88 | -1.35 | 7.22 | 90 | 76 | 21.8 | 9.09 | 18.74 | 3.61 | 8.06 | 3504.62 | 1050.13 | 1311.54 | 764.4 | 10.76 | 1.65 | 4.31 | 71.56 | 680 | 5900 | 82.02 | 0.59 | 11.62 | 83.76 | 60 | 9 | 9 | 0.38 | 408 | 411.38 | 381020.78 | 363052.89 | 20230204-163228_f4d9136d-7c5f-4115-bed5-81e02ade9b44 | 1.0256
21.95 | 31.15 | 5505.78 | 7.6 | [18.84, 48.62] | [24.88, 1.11] | [12.86, 12.86] | [3.62, 9.63] | 0 | 596.38 | 56.58 | 62.59 | -6.01 | 7.19 | 90.07 | 89 | 18.9 | 9.2 | 17.56 | 4.38 | 9.23 | 3523.7 | 1064.21 | 1397.95 | 790.03 | 5.88 | 1.67 | 4.26 | 67.74 | 680 | 5900 | 83.05 | 0.59 | 10.09 | 48.94 | 60 | 9 | 9 | 0.64 | 408 | 413.78 | 369704 | 165330.6 | 20230204-163228_44f0f0bd-fd82-44c2-9d63-55e7a60fb289 | 11.6651
22.38 | 31.46 | 5472.19 | 7.61 | [22.53, 30.59] | [24.96, 17.46] | [13.0, 13.0] | [5.54, 6.11] | 0 | 652.4 | 60.49 | 61.05 | -0.56 | 7.22 | 90.02 | 71 | 22.2 | 9.08 | 18.46 | 3.92 | 8.39 | 3502.2 | 1053.57 | 1346.38 | 774.17 | 9.91 | 1.67 | 4.27 | 69.87 | 680 | 5900 | 82 | 0.59 | 11.1 | 77.18 | 60 | 9 | 9 | 0.41 | 408 | 411.66 | 393621.57 | 314414.15 | 20230204-163228_392e2257-671b-4dee-85c8-35d8b238f46b | 4.521
21.82 | 31.02 | 5506.44 | 7.59 | [18.11, 47.74] | [24.83, 0.92] | [12.8, 12.8] | [3.73, 9.45] | 0 | 584.81 | 55.74 | 61.46 | -5.72 | 7.18 | 90 | 90 | 18.8 | 9.2 | 17.59 | 4.24 | 9.42 | 3524.12 | 1065.25 | 1407.74 | 792.57 | 5.89 | 1.67 | 4.26 | 68.46 | 680 | 5900 | 83.03 | 0.59 | 9.87 | 49.84 | 60 | 9 | 9 | 0.63 | 408 | 413.67 | 369518.81 | 160381.91 | 20230204-163228_1d886f71-5eac-4070-a368-052da601ac6c | 11.937
22.68 | 31.59 | 5492.7 | 7.6 | [17.02, 29.66] | [24.96, 13.71] | [12.79, 12.79] | [4.52, 5.91] | 0 | 564.59 | 54.77 | 56.16 | -1.39 | 7.16 | 90.19 | 85 | 20.1 | 8.91 | 18.25 | 4.43 | 9.73 | 3515.33 | 1064.25 | 1421.83 | 795.06 | 9.26 | 1.69 | 4.21 | 66.78 | 680 | 5900 | 80.43 | 0.59 | 9.21 | 79.72 | 60 | 9 | 9 | 0.39 | 408 | 411.55 | 378163.57 | 265356.03 | 20230204-163228_5af75082-cda2-4678-a54d-ff0127ab1b83 | 6.4388
22.63 | 31.75 | 5471.38 | 7.6 | [27.38, 30.8] | [24.98, 22.24] | [11.65, 11.65] | [5.47, 6.16] | 0 | 726.98 | 64.01 | 64.69 | -0.68 | 7.25 | 89.96 | 77 | 22.2 | 9.12 | 19.25 | 3.38 | 7.53 | 3501.69 | 1046.57 | 1282.29 | 756.58 | 10.39 | 1.64 | 4.32 | 72.95 | 680 | 5900 | 82.29 | 0.59 | 12.61 | 76.49 | 60 | 9 | 9 | 0.41 | 408 | 411.7 | 396153.08 | 372586.36 | 20230204-163228_e4972e1b-d56c-4881-86fe-46218ff5ef74 | 1.3451
22.67 | 31.65 | 5489.74 | 7.6 | [17.65, 46.83] | [24.9, 0.54] | [12.91, 12.91] | [4.46, 9.27] | 0 | 575.71 | 55.46 | 60.28 | -4.82 | 7.17 | 89.9 | 81 | 21.4 | 8.97 | 19 | 3.67 | 9.54 | 3513.43 | 1063 | 1413.06 | 792.73 | 5.98 | 1.69 | 4.22 | 70.96 | 680 | 5900 | 80.99 | 0.59 | 9.49 | 50.82 | 60 | 9 | 9 | 0.62 | 408 | 413.56 | 377438.45 | 153172.19 | 20230204-163228_961034e0-fa5a-4d68-a862-515841e08b48 | 12.8006
22.67 | 31.73 | 5515.55 | 7.63 | [22.3, 49.39] | [25.08, 1.82] | [12.39, 12.39] | [5.96, 9.78] | 0 | 651.39 | 59.77 | 63.6 | -3.83 | 7.21 | 89.86 | 91 | 20.2 | 9.06 | 19.09 | 3.58 | 8.47 | 3529.95 | 1060.74 | 1348.68 | 777.57 | 6.11 | 1.69 | 4.24 | 71.7 | 680 | 5900 | 81.78 | 0.59 | 10.95 | 48.17 | 60 | 9 | 9 | 0.65 | 408 | 413.87 | 398480.05 | 175828.62 | 20230204-163228_8e8ac34c-987e-4707-bd39-e67a22fd5063 | 12.7084
22.35 | 31.3 | 5520.8 | 7.6 | [19.94, 47.49] | [24.64, 0.96] | [12.69, 12.69] | [5.53, 9.41] | 0 | 617.63 | 57.27 | 61.14 | -3.87 | 7.2 | 89.98 | 95 | 18.9 | 8.95 | 18.29 | 4.06 | 8.94 | 3533.31 | 1065.26 | 1383.07 | 787.31 | 6.09 | 1.68 | 4.25 | 68.82 | 680 | 5900 | 80.83 | 0.59 | 10.18 | 50.1 | 60 | 9 | 9 | 0.63 | 408 | 413.64 | 386996.07 | 160073.87 | 20230204-163228_b4cd858d-cbe2-462f-b0a3-1e74a4df1bca | 12.9522
21.84 | 30.99 | 5521.67 | 7.6 | [19.63, 25.6] | [25.38, 20.65] | [12.7, 12.7] | [3.89, 5.13] | 0 | 605.27 | 57.71 | 58.95 | -1.24 | 7.18 | 89.99 | 90 | 19 | 9.15 | 17.78 | 4.06 | 9.12 | 3533.87 | 1065.66 | 1387.98 | 788.3 | 11.26 | 1.67 | 4.27 | 69.28 | 680 | 5900 | 82.59 | 0.59 | 10.17 | 91.93 | 60 | 9 | 9 | 0.34 | 408 | 411.08 | 379132.88 | 338903.07 | 20230204-163228_6d69ac3d-5298-427f-9cd3-2d5b0d1ca158 | 2.2962
22.03 | 31.11 | 5529.43 | 7.6 | [17.44, 20.22] | [25.11, 21.8] | [12.85, 12.85] | [4.59, 4.07] | 0 | 570.27 | 55.4 | 54.87 | 0.53 | 7.17 | 90.06 | 94 | 18.6 | 9.08 | 17.87 | 4.15 | 9.7 | 3538.84 | 1070.81 | 1425.63 | 798.89 | 13.63 | 1.68 | 4.23 | 68.63 | 680 | 5900 | 81.98 | 0.59 | 9.43 | 115.93 | 60 | 9 | 9 | 0.27 | 408 | 410.44 | 381110.13 | 337675.01 | 20230204-163228_6f48bf9a-3fb6-48df-8f49-6f2209e4b3af | 2.4792
22.28 | 31.5 | 5499.84 | 7.59 | [20.2, 50.0] | [25.01, 1.6] | [12.78, 12.78] | [3.53, 9.9] | 0 | 617.68 | 57.99 | 64.38 | -6.39 | 7.2 | 90 | 87 | 19.7 | 9.22 | 18.1 | 4.17 | 8.9 | 3519.9 | 1061 | 1376.29 | 783.83 | 5.86 | 1.66 | 4.27 | 68.83 | 680 | 5900 | 83.22 | 0.59 | 10.53 | 47.58 | 60 | 9 | 9 | 0.66 | 408 | 413.94 | 371483.98 | 175251.06 | 20230204-163228_05325a78-0675-4039-8882-cffcc3b78bc6 | 11.2005
22.56 | 31.62 | 5492.35 | 7.62 | [29.93, 55.82] | [24.5, 3.43] | [12.65, 12.65] | [6.24, 11.06] | 0 | 756.45 | 67.08 | 71.9 | -4.82 | 7.29 | 89.98 | 75 | 21.9 | 9.06 | 18.7 | 3.85 | 7.26 | 3515.1 | 1050.92 | 1284.9 | 759.76 | 6.06 | 1.66 | 4.3 | 70.17 | 680 | 5900 | 81.78 | 0.59 | 13.06 | 42.6 | 60 | 9 | 9 | 0.74 | 408 | 414.64 | 401198.53 | 214417.05 | 20230204-163228_c57d0b80-8e56-42bc-8721-1c36d262d6ef | 10.661
22.44 | 31.58 | 5472.56 | 7.6 | [26.35, 48.56] | [25.04, 7.41] | [11.48, 11.48] | [5.06, 9.63] | 0 | 714.21 | 62.87 | 67.45 | -4.58 | 7.24 | 90.03 | 75 | 22.2 | 9.13 | 18.99 | 3.45 | 7.66 | 3502.44 | 1047.13 | 1287.25 | 757.77 | 6.53 | 1.64 | 4.33 | 72.56 | 680 | 5900 | 82.45 | 0.59 | 12.37 | 48.91 | 60 | 9 | 9 | 0.64 | 408 | 413.78 | 391684.52 | 241386.99 | 20230204-163228_b5a51695-f7fc-43bc-b477-c4f3e78d5541 | 8.5786
22.47 | 31.55 | 5473.72 | 7.6 | [23.87, 43.35] | [25.01, 9.46] | [11.76, 11.76] | [4.67, 8.61] | 0 | 678.79 | 60.64 | 64.57 | -3.93 | 7.22 | 90.05 | 77 | 21.8 | 9.08 | 18.87 | 3.6 | 8.06 | 3503.18 | 1049.86 | 1312.32 | 764.48 | 7.04 | 1.65 | 4.3 | 71.59 | 680 | 5900 | 81.95 | 0.59 | 11.6 | 54.73 | 60 | 9 | 9 | 0.57 | 408 | 413.17 | 385291.22 | 251834.55 | 20230204-163228_34a68c8f-5108-4dd4-9e08-83271423bc71 | 7.6174
22.59 | 31.63 | 5474.42 | 7.6 | [23.45, 23.18] | [25.33, 24.3] | [13.06, 13.06] | [5.96, 4.66] | 0 | 661.68 | 61.84 | 60.54 | 1.3 | 7.23 | 90.11 | 72 | 22.2 | 9.05 | 18.59 | 3.99 | 8.27 | 3503.63 | 1053.13 | 1338.65 | 772.24 | 13.28 | 1.66 | 4.28 | 69.39 | 680 | 5900 | 81.69 | 0.59 | 11.23 | 101.19 | 60 | 9 | 9 | 0.31 | 408 | 410.79 | 403165.45 | 377112.17 | 20230204-163228_cc6641b5-feb8-4e28-8b26-7e4531ffb807 | 1.4871
22.35 | 31.48 | 5494.74 | 7.6 | [20.44, 24.76] | [25.04, 22.12] | [12.69, 12.69] | [3.57, 4.96] | 0 | 621.67 | 58.17 | 59.57 | -1.4 | 7.2 | 90.02 | 87 | 20 | 9.13 | 18.4 | 3.95 | 8.84 | 3516.63 | 1059.51 | 1370.39 | 781.82 | 11.72 | 1.67 | 4.26 | 69.79 | 680 | 5900 | 82.4 | 0.59 | 10.51 | 94.93 | 60 | 9 | 9 | 0.33 | 408 | 410.98 | 372327.45 | 354490.97 | 20230204-163228_8e3e2b9d-9802-44f5-9363-e1daa40f923d | 1.0181
22.61 | 31.58 | 5473.48 | 7.6 | [24.37, 36.17] | [25.26, 15.83] | [12.85, 12.85] | [4.84, 7.21] | 0 | 676.54 | 62.48 | 64.85 | -2.37 | 7.23 | 90.09 | 69 | 22.6 | 8.97 | 18.57 | 4.04 | 8.09 | 3503.03 | 1051.65 | 1326.04 | 768.77 | 8.67 | 1.66 | 4.29 | 68.97 | 680 | 5900 | 80.99 | 0.59 | 11.42 | 65.39 | 60 | 9 | 9 | 0.48 | 408 | 412.32 | 391574.71 | 310376.1 | 20230204-163228_567ee266-6182-44d0-ba87-68d0b96308dd | 4.6346
22.09 | 31.15 | 5534.31 | 7.6 | [19.78, 35.32] | [25.2, 11.61] | [12.79, 12.79] | [5.07, 7.03] | 0 | 609.07 | 57.77 | 59.72 | -1.95 | 7.19 | 89.98 | 94 | 18.7 | 9.06 | 17.97 | 4.12 | 9.09 | 3541.96 | 1068.16 | 1390.69 | 790.15 | 8.22 | 1.67 | 4.25 | 68.73 | 680 | 5900 | 81.76 | 0.59 | 10.11 | 67.07 | 60 | 9 | 9 | 0.47 | 408 | 412.22 | 389094.72 | 255981.51 | 20230204-163228_ab778cfe-e213-44de-aaf0-af4f25431fe8 | 7.5978
22.41 | 31.43 | 5478.1 | 7.6 | [26.42, 26.42] | [24.74, 24.74] | [12.53, 12.53] | [5.17, 5.17] | 0 | 711.5 | 63.69 | 63.69 | 0 | 7.26 | 89.89 | 70 | 22.5 | 9.02 | 18.61 | 3.8 | 7.7 | 3505.98 | 1050.3 | 1304.33 | 763.49 | 12.31 | 1.64 | 4.32 | 70.38 | 680 | 5900 | 81.46 | 0.59 | 12.16 | 91.09 | 60 | 9 | 9 | 0.34 | 408 | 411.1 | 390067.36 | 390067.36 | 20230204-163228_7d42abf7-549f-4481-94b0-d74d24357abe | 0
22.14 | 31.34 | 5503.38 | 7.6 | [22.51, 52.34] | [25.34, 2.3] | [12.76, 12.76] | [3.57, 10.37] | 0 | 649.8 | 60.61 | 67.4 | -6.79 | 7.22 | 89.97 | 88 | 19.3 | 9.21 | 17.84 | 4.3 | 8.47 | 3522.16 | 1058.97 | 1350.17 | 777.22 | 5.84 | 1.66 | 4.28 | 68.15 | 680 | 5900 | 83.11 | 0.59 | 11.13 | 45.44 | 60 | 9 | 9 | 0.69 | 408 | 414.22 | 377950.97 | 190657.57 | 20230204-163228_084d391c-0574-44fc-983f-3db91734c9a8 | 10.6903
22.35 | 31.43 | 5480.89 | 7.6 | [22.47, 36.95] | [25.01, 13.92] | [11.65, 11.65] | [3.96, 7.36] | 0 | 659.12 | 59.13 | 62.52 | -3.39 | 7.2 | 90.02 | 82 | 20.7 | 9.08 | 18.45 | 3.9 | 8.32 | 3507.77 | 1052.23 | 1325.17 | 768.21 | 8.04 | 1.65 | 4.3 | 69.95 | 680 | 5900 | 81.93 | 0.59 | 11.2 | 64.07 | 60 | 9 | 9 | 0.49 | 408 | 412.41 | 376810.22 | 288059.59 | 20230204-163228_232f0df2-d2fd-4d6a-9561-76ac96f8409f | 5.0657
22.05 | 31.13 | 5517.81 | 7.6 | [20.9, 24.53] | [24.66, 21.7] | [12.78, 12.78] | [4.26, 4.92] | 0 | 632.21 | 58.34 | 59.01 | -0.67 | 7.21 | 89.97 | 91 | 19.3 | 9.09 | 18.2 | 3.84 | 8.73 | 3531.4 | 1063.73 | 1372 | 784.29 | 11.87 | 1.67 | 4.27 | 70.27 | 680 | 5900 | 82.02 | 0.59 | 10.61 | 95.83 | 60 | 9 | 9 | 0.33 | 408 | 410.95 | 375294.47 | 348734.9 | 20230204-163228_ef90db46-46d1-4da8-8236-3e2a514ce119 | 1.516
22.6 | 31.7 | 5514.38 | 7.56 | [25.97, 53.29] | [25.0, 2.06] | [13.27, 13.27] | [6.18, 10.56] | 0 | 698.11 | 64.24 | 68.62 | -4.38 | 7.26 | 89.89 | 82 | 21.2 | 9.1 | 18.94 | 3.66 | 7.9 | 3529.2 | 1059.05 | 1328.5 | 773.01 | 6.09 | 1.62 | 4.33 | 71.31 | 680 | 5900 | 82.18 | 0.59 | 11.91 | 44.64 | 60 | 9 | 9 | 0.7 | 408 | 414.33 | 403858.19 | 190831 | 20230204-163228_211f9cc0-c6b3-48d3-91a3-1ed4d03c7f63 | 12.1591
22.41 | 31.2 | 5492.1 | 7.61 | [13.3, 37.05] | [19.92, 1.51] | [12.82, 12.82] | [2.01, 7.34] | 0 | 543.62 | 46.04 | 51.38 | -5.34 | 7.21 | 90.26 | 89 | 20.2 | 8.79 | 18.84 | 3.57 | 10.1 | 3514.94 | 1073.74 | 1497.61 | 818 | 6.27 | 1.72 | 4.17 | 71.11 | 680 | 5900 | 79.33 | 0.59 | 8.71 | 64.21 | 60 | 9 | 9 | 0.49 | 408 | 412.4 | 287596.97 | 136824.64 | 20230204-163852_8ad59907-34b7-4839-9946-9cfea0696c68 | 8.6057
22.16 | 30.96 | 5534.31 | 7.6 | [16.33, 39.26] | [19.84, 2.44] | [12.76, 12.76] | [2.26, 7.78] | 0 | 606.38 | 48.93 | 54.46 | -5.53 | 7.24 | 89.89 | 91 | 19.9 | 8.8 | 18.79 | 3.37 | 9.13 | 3541.96 | 1075.04 | 1441.36 | 806.25 | 6.29 | 1.69 | 4.22 | 72.31 | 680 | 5900 | 79.4 | 0.59 | 9.77 | 60.57 | 60 | 9 | 9 | 0.52 | 408 | 412.67 | 291769.89 | 154544.08 | 20230204-163852_a0238ab2-eec5-4580-a9b7-395b2a5cf700 | 7.8325
21.55 | 30.52 | 5538.19 | 7.59 | [35.68, 49.83] | [15.04, 1.44] | [12.89, 12.89] | [9.33, 9.87] | 0 | 932.9 | 63.61 | 64.16 | -0.55 | 7.49 | 90.17 | 69 | 21.8 | 8.96 | 17.83 | 3.73 | 5.94 | 3544.44 | 1058.42 | 1263.72 | 760.71 | 6.44 | 1.61 | 4.37 | 70.62 | 680 | 5900 | 80.91 | 0.59 | 16.39 | 47.74 | 60 | 9 | 9 | 0.66 | 408 | 413.92 | 321789.47 | 172859.81 | 20230204-163852_9313205f-ffd4-482a-8e4b-90190fe206c2 | 8.5006
22.56 | 31.51 | 5478.79 | 7.6 | [25.79, 25.79] | [20.01, 20.01] | [12.73, 12.73] | [2.22, 2.22] | 0 | 755.68 | 58.53 | 58.53 | 0 | 7.33 | 89.88 | 67 | 22.7 | 8.95 | 18.39 | 4.17 | 7.25 | 3506.43 | 1052.28 | 1310.57 | 767.11 | 26.33 | 1.65 | 4.3 | 68.21 | 680 | 5900 | 80.77 | 0.59 | 12.92 | 211.99 | 60 | 9 | 9 | 0.15 | 408 | 409.33 | 301774.36 | 301774.36 | 20230204-163852_1304ddfc-af5f-4c90-81db-1d63ad22f719 | 0
21.66 | 30.7 | 5551 | 7.59 | [39.16, 51.75] | [15.03, 2.69] | [12.21, 12.21] | [10.0, 10.25] | 0 | 971.31 | 66.4 | 66.65 | -0.25 | 7.5 | 89.96 | 70 | 21.7 | 9.05 | 17.86 | 3.79 | 5.71 | 3552.64 | 1058.31 | 1244.17 | 756.09 | 6.48 | 1.61 | 4.38 | 70.46 | 680 | 5900 | 81.68 | 0.59 | 17.32 | 45.95 | 60 | 9 | 9 | 0.68 | 408 | 414.15 | 330965.92 | 193252.12 | 20230204-163852_ad8b0826-c7db-4aa8-9ca0-ed0a3d544bb5 | 7.8604
21.74 | 30.56 | 5552.1 | 7.61 | [41.49, 56.86] | [14.99, 0.88] | [9.82, 9.82] | [10.0, 11.26] | 0 | 1016.02 | 66.3 | 67.56 | -1.26 | 7.49 | 89.98 | 71 | 21.7 | 8.82 | 17.99 | 3.75 | 5.46 | 3553.35 | 1054.36 | 1210.01 | 746.09 | 5.89 | 1.61 | 4.39 | 70.2 | 680 | 5900 | 79.64 | 0.59 | 17.84 | 41.84 | 60 | 9 | 9 | 0.75 | 408 | 414.76 | 330424.19 | 183671.18 | 20230204-163852_84c1a374-b60c-4693-b453-c83eb51da72b | 8.3763
21.78 | 30.72 | 5547.17 | 7.6 | [39.52, 52.26] | [15.03, 2.65] | [12.4, 12.4] | [10.0, 10.36] | 0 | 972.39 | 66.95 | 67.31 | -0.36 | 7.5 | 89.98 | 69 | 22 | 8.94 | 18.01 | 3.77 | 5.7 | 3550.19 | 1057.71 | 1244.16 | 755.86 | 6.47 | 1.62 | 4.37 | 70.36 | 680 | 5900 | 80.74 | 0.59 | 17.16 | 45.5 | 60 | 9 | 9 | 0.69 | 408 | 414.21 | 331476.54 | 194327.47 | 20230204-163852_1fd1339f-62ab-4dcb-8781-3a8d1dbcf50a | 7.8281
22.07 | 31.09 | 5548.01 | 7.6 | [37.15, 37.93] | [14.82, 13.55] | [12.68, 12.68] | [8.04, 7.55] | 0 | 951.85 | 64.65 | 64.16 | 0.49 | 7.5 | 89.94 | 75 | 21.7 | 9.02 | 18.52 | 3.56 | 5.83 | 3550.72 | 1059.31 | 1256.8 | 759.54 | 8.56 | 1.63 | 4.35 | 71.7 | 680 | 5900 | 81.39 | 0.59 | 16.86 | 62.43 | 60 | 9 | 9 | 0.5 | 408 | 412.53 | 307086.95 | 287246.86 | 20230204-163852_78835765-2c43-408f-bd6e-32bdbc233ece | 1.1324
21.84 | 30.36 | 5558.86 | 7.6 | [45.97, 45.97] | [15.0, 15.0] | [8.54, 8.54] | [10.0, 10.0] | 0 | 1062.82 | 69.51 | 69.51 | 0 | 7.5 | 89.97 | 71 | 21.6 | 8.52 | 17.9 | 3.94 | 5.23 | 3557.67 | 1052.84 | 1187.21 | 740.06 | 6.95 | 1.59 | 4.41 | 68.4 | 680 | 5900 | 76.95 | 0.59 | 18.19 | 47.13 | 60 | 9 | 9 | 0.67 | 408 | 414 | 333335.56 | 333335.56 | 20230204-163852_57893447-e073-4651-a9f3-1eb7a23f4001 | 0
22.28 | 31.27 | 5464.31 | 7.59 | [22.29, 43.97] | [24.99, 8.96] | [12.56, 12.56] | [3.09, 8.73] | 0 | 651.14 | 59.84 | 65.49 | -5.65 | 7.22 | 90.01 | 69 | 22.4 | 8.99 | 18.38 | 3.89 | 8.39 | 3497.16 | 1051.29 | 1339.19 | 771.31 | 6.85 | 1.65 | 4.3 | 69.78 | 680 | 5900 | 81.16 | 0.59 | 10.98 | 53.97 | 60 | 9 | 9 | 0.58 | 408 | 413.24 | 368419.37 | 248073.45 | 20230204-163852_872877e1-d342-4fbe-9992-136e0723f9d9 | 6.8691
22 | 30.51 | 5556.16 | 7.6 | [44.75, 44.75] | [14.99, 14.99] | [8.75, 8.75] | [10.0, 10.0] | 0 | 1052.16 | 68.49 | 68.49 | 0 | 7.5 | 90.04 | 68 | 22 | 8.51 | 17.88 | 4.13 | 5.28 | 3555.95 | 1052.87 | 1191.37 | 741.03 | 6.85 | 1.6 | 4.4 | 67.34 | 680 | 5900 | 76.81 | 0.59 | 17.94 | 47.11 | 60 | 9 | 9 | 0.67 | 408 | 414 | 332336.01 | 332336.01 | 20230204-163852_27fbb9ed-067a-4ce1-a42b-25e407e39ad5 | 0
21.74 | 30.74 | 5543.42 | 7.61 | [43.5, 57.13] | [15.1, 4.06] | [12.41, 12.41] | [8.74, 11.32] | 0 | 1003.25 | 71.01 | 73.6 | -2.59 | 7.52 | 89.86 | 67 | 22.3 | 8.99 | 18.02 | 3.72 | 5.53 | 3547.79 | 1055.56 | 1229.99 | 751.69 | 6.27 | 1.61 | 4.38 | 70.74 | 680 | 5900 | 81.2 | 0.59 | 17.94 | 41.62 | 60 | 9 | 9 | 0.75 | 408 | 414.79 | 323009.73 | 225783.56 | 20230204-163852_e594e12f-a023-458f-933c-e78567b3faaf | 5.5494
22.48 | 31.44 | 5470.56 | 7.6 | [20.65, 37.55] | [24.96, 12.92] | [13.03, 13.03] | [2.61, 7.47] | 0 | 623.78 | 58.64 | 63.5 | -4.86 | 7.21 | 90.03 | 70 | 22.5 | 8.96 | 18.61 | 3.87 | 8.77 | 3501.16 | 1055.44 | 1368.18 | 779.71 | 7.85 | 1.67 | 4.26 | 69.86 | 680 | 5900 | 80.9 | 0.59 | 10.41 | 63.07 | 60 | 9 | 9 | 0.5 | 408 | 412.48 | 362181.43 | 278698.54 | 20230204-163852_614230fe-fc29-4f43-b2ec-be9f90d430a5 | 4.765
22.43 | 31.31 | 5552.86 | 7.58 | [20.59, 44.28] | [18.03, 0.17] | [12.55, 12.55] | [2.95, 8.77] | 0 | 705.62 | 51.17 | 57 | -5.83 | 7.32 | 89.92 | 92 | 19.9 | 8.88 | 18.92 | 3.51 | 7.87 | 3553.83 | 1071.95 | 1376.41 | 791.08 | 5.84 | 1.66 | 4.26 | 71.65 | 680 | 5900 | 80.16 | 0.59 | 11.67 | 53.74 | 60 | 9 | 9 | 0.58 | 408 | 413.26 | 280129.77 | 140925.53 | 20230204-163852_8ff3e106-9b4e-4f3c-a4e5-10f8fd65d6c8 | 7.9454
21.73 | 30.04 | 5555.96 | 7.6 | [44.51, 56.87] | [15.0, 3.91] | [6.85, 6.85] | [10.0, 11.27] | 0 | 1071.91 | 66.36 | 67.63 | -1.27 | 7.48 | 89.93 | 71 | 21.8 | 8.31 | 18.09 | 3.64 | 5.18 | 3555.82 | 1050.34 | 1171.63 | 735.03 | 5.89 | 1.58 | 4.43 | 69.52 | 680 | 5900 | 75.01 | 0.59 | 17.93 | 41.81 | 60 | 9 | 9 | 0.75 | 408 | 414.76 | 330537.01 | 218332.8 | 20230204-163852_6b79eb15-c747-46dd-b538-1f564e6d7aab | 6.4043
22.45 | 31.54 | 5458.06 | 7.6 | [21.47, 50.88] | [24.87, 1.85] | [12.79, 12.79] | [3.7, 10.08] | 0 | 638.84 | 59.13 | 65.52 | -6.39 | 7.21 | 90.04 | 68 | 22.1 | 9.09 | 17.97 | 4.48 | 8.54 | 3493.16 | 1051.52 | 1350.67 | 774.04 | 5.87 | 1.67 | 4.27 | 67.01 | 680 | 5900 | 82.09 | 0.59 | 10.88 | 46.76 | 60 | 9 | 9 | 0.67 | 408 | 414.05 | 372594.83 | 180841.42 | 20230204-163852_b4201c25-4eac-4d7f-b1da-c17070788bbc | 10.9448
22.49 | 31.41 | 5484.36 | 7.6 | [25.89, 25.89] | [20.17, 20.17] | [12.68, 12.68] | [2.01, 2.01] | 0 | 755.44 | 58.74 | 58.74 | 0 | 7.33 | 90.04 | 70 | 22.5 | 8.92 | 18.61 | 3.88 | 7.26 | 3509.99 | 1053.14 | 1310.4 | 767.4 | 29.21 | 1.65 | 4.3 | 69.72 | 680 | 5900 | 80.55 | 0.59 | 12.87 | 234.29 | 60 | 9 | 9 | 0.13 | 408 | 409.21 | 301637.97 | 301637.97 | 20230204-163852_21dfcd71-d61f-4eac-9b8e-58136c6f9045 | 0
22.4 | 31.36 | 5553.38 | 7.61 | [29.71, 43.47] | [14.81, 3.99] | [12.87, 12.87] | [5.67, 8.62] | 0 | 873.61 | 57.39 | 60.33 | -2.94 | 7.46 | 90.03 | 80 | 21.1 | 8.96 | 18.59 | 3.81 | 6.36 | 3554.16 | 1064.84 | 1299.35 | 771.7 | 6.66 | 1.65 | 4.3 | 70.14 | 680 | 5900 | 80.88 | 0.59 | 15.1 | 54.67 | 60 | 9 | 9 | 0.57 | 408 | 413.17 | 276558.05 | 185877.46 | 20230204-163852_683d379c-0c81-4f9b-8c14-b13444fa99b3 | 5.1758
22.83 | 31.77 | 5476.4 | 7.6 | [25.94, 54.73] | [25.17, 3.05] | [12.72, 12.72] | [4.18, 10.84] | 0 | 699.52 | 63.83 | 70.5 | -6.67 | 7.25 | 89.9 | 74 | 21.9 | 8.95 | 18.57 | 4.25 | 7.83 | 3504.9 | 1050.64 | 1310.93 | 765.04 | 5.89 | 1.65 | 4.29 | 67.78 | 680 | 5900 | 80.77 | 0.59 | 11.83 | 43.45 | 60 | 9 | 9 | 0.72 | 408 | 414.51 | 385037.34 | 206635.4 | 20230204-163852_93192c66-2e60-4b7d-9c3f-3cbb3931a92c | 10.1828
22.35 | 31.32 | 5566.05 | 7.61 | [27.49, 47.56] | [15.16, 0.68] | [12.98, 12.98] | [3.84, 9.42] | 0 | 840.53 | 55.63 | 61.22 | -5.59 | 7.44 | 89.85 | 92 | 20 | 8.97 | 19.02 | 3.33 | 6.62 | 3562.27 | 1069.08 | 1319.57 | 778.11 | 5.91 | 1.67 | 4.28 | 72.91 | 680 | 5900 | 80.98 | 0.59 | 14.4 | 50.04 | 60 | 9 | 9 | 0.63 | 408 | 413.65 | 260433.24 | 157084.95 | 20230204-163852_54809292-d8b5-488b-b6f3-8afb0c7150f5 | 5.8989
21.85 | 30.82 | 5551.18 | 7.6 | [38.43, 37.3] | [14.96, 13.51] | [12.28, 12.28] | [10.0, 7.42] | 0 | 965.25 | 65.67 | 63.09 | 2.58 | 7.5 | 90.02 | 73 | 21.5 | 8.98 | 18.07 | 3.78 | 5.75 | 3552.76 | 1058.75 | 1247.76 | 757.13 | 8.85 | 1.61 | 4.37 | 70.36 | 680 | 5900 | 81.02 | 0.59 | 17.05 | 63.49 | 60 | 9 | 9 | 0.49 | 408 | 412.45 | 329481.54 | 284588.43 | 20230204-163852_93e25903-9081-437c-909a-bb62432b2205 | 2.5624
21.74 | 30.66 | 5545.72 | 7.61 | [37.86, 50.81] | [14.95, 2.18] | [12.44, 12.44] | [9.88, 10.07] | 0 | 958.8 | 65.25 | 65.43 | -0.18 | 7.49 | 89.93 | 68 | 22 | 8.91 | 17.88 | 3.86 | 5.78 | 3549.26 | 1058.19 | 1250.63 | 757.56 | 6.48 | 1.62 | 4.36 | 69.76 | 680 | 5900 | 80.47 | 0.59 | 16.82 | 46.82 | 60 | 9 | 9 | 0.67 | 408 | 414.04 | 327766.87 | 184442.71 | 20230204-163852_9ab28186-2862-4a22-956c-3c4522b45ac2 | 8.1806
22.31 | 31.25 | 5554.54 | 7.6 | [33.4, 36.76] | [15.19, 12.68] | [12.73, 12.73] | [6.48, 7.31] | 0 | 909.75 | 61.32 | 62.17 | -0.85 | 7.47 | 89.93 | 79 | 21.5 | 8.95 | 18.84 | 3.47 | 6.11 | 3554.91 | 1062.46 | 1276.55 | 765.35 | 8.39 | 1.64 | 4.33 | 72.07 | 680 | 5900 | 80.75 | 0.59 | 15.82 | 64.44 | 60 | 9 | 9 | 0.49 | 408 | 412.39 | 292573.11 | 273154.05 | 20230204-163852_be190a79-6a95-47c8-b05f-e74f9439b3bc | 1.1084
21.84 | 30.8 | 5546.62 | 7.61 | [38.85, 51.56] | [15.0, 2.5] | [12.34, 12.34] | [10.0, 10.22] | 0 | 967.78 | 66.19 | 66.4 | -0.21 | 7.5 | 90 | 73 | 21.8 | 8.95 | 18.35 | 3.49 | 5.73 | 3549.84 | 1057.79 | 1245.81 | 756.26 | 6.48 | 1.63 | 4.36 | 71.93 | 680 | 5900 | 80.82 | 0.59 | 17.08 | 46.13 | 60 | 9 | 9 | 0.68 | 408 | 414.13 | 330448.26 | 190508.62 | 20230204-163852_71345143-f3b8-45fa-a817-ff2dc27eaef5 | 7.9874
22.38 | 31.32 | 5553.21 | 7.61 | [34.73, 46.92] | [15.01, 4.82] | [13.38, 13.38] | [7.3, 9.3] | 0 | 919.3 | 63.12 | 65.12 | -2 | 7.49 | 89.99 | 76 | 21.8 | 8.94 | 18.74 | 3.64 | 6.04 | 3554.06 | 1062.56 | 1277.79 | 765.88 | 6.78 | 1.65 | 4.31 | 71.05 | 680 | 5900 | 80.7 | 0.59 | 16.01 | 50.65 | 60 | 9 | 9 | 0.62 | 408 | 413.58 | 300336.5 | 206517.48 | 20230204-163852_2c7361aa-55cf-4672-8dbb-35bfdde4aaa8 | 5.355
22.54 | 31.49 | 5560.7 | 7.6 | [32.03, 50.04] | [15.02, 2.1] | [12.3, 12.3] | [4.83, 9.91] | 0 | 902.08 | 59.35 | 64.44 | -5.09 | 7.46 | 89.92 | 84 | 21.2 | 8.95 | 19.19 | 3.35 | 6.16 | 3558.85 | 1063.73 | 1279.5 | 766.51 | 5.99 | 1.64 | 4.32 | 72.77 | 680 | 5900 | 80.78 | 0.59 | 15.64 | 47.53 | 60 | 9 | 9 | 0.66 | 408 | 413.95 | 272090.2 | 181075.41 | 20230204-163852_29dfe2b2-e8b3-40a5-bdb4-8bdca9b16afb | 5.1949
20.22 | 28.82 | 5723.31 | 7.59 | [42.73, 42.73] | [14.99, 14.99] | [8.75, 8.75] | [5.0, 5.0] | 0 | 1037.39 | 66.47 | 66.47 | 0 | 7.49 | 88.92 | 64 | 19.2 | 8.6 | 14.79 | 5.43 | 5.52 | 3662.92 | 1085.01 | 1231.9 | 764.56 | 13.3 | 1.58 | 4.43 | 61.3 | 680 | 5900 | 77.64 | 0.59 | 17.19 | 94.31 | 60 | 9 | 9 | 0.33 | 408 | 411 | 279667.1 | 279667.1 | 20230204-164514_80d71a9e-77a5-407d-8711-3581c0b54066 | 0
21.27 | 29.87 | 5661.41 | 7.61 | [35.41, 35.41] | [15.0, 15.0] | [9.82, 9.82] | [5.0, 5.0] | 0 | 963.03 | 60.23 | 60.23 | 0 | 7.46 | 89.93 | 74 | 18.8 | 8.6 | 15.65 | 5.62 | 5.88 | 3623.3 | 1077.15 | 1253.68 | 766.07 | 12.05 | 1.62 | 4.37 | 60.48 | 680 | 5900 | 77.62 | 0.59 | 15.91 | 94.29 | 60 | 9 | 9 | 0.33 | 408 | 411 | 274384.49 | 274384.49 | 20230204-164514_14fce8ee-f0ec-4a1f-8f9b-92d3d9e56dde | 0
22.3 | 30.75 | 5612.7 | 7.6 | [42.7, 59.33] | [15.0, 2.92] | [8.28, 8.28] | [7.2, 11.76] | 0 | 1042.2 | 65.98 | 70.53 | -4.55 | 7.48 | 90.12 | 68 | 22 | 8.45 | 17.88 | 4.42 | 5.39 | 3592.13 | 1063.4 | 1203 | 748.24 | 5.61 | 1.61 | 4.38 | 65.63 | 680 | 5900 | 76.26 | 0.59 | 17.39 | 40.09 | 60 | 9 | 9 | 0.78 | 408 | 415.05 | 301820.31 | 214479.08 | 20230204-164514_5157bb7f-81bb-4b1c-a388-15bd93914918 | 4.9852
22.76 | 31.25 | 5640.88 | 7.61 | [29.33, 44.12] | [14.99, 3.95] | [8.79, 8.79] | [5.0, 8.75] | 0 | 910.07 | 53.11 | 56.86 | -3.75 | 7.41 | 89.99 | 72 | 21.7 | 8.49 | 18.13 | 4.64 | 6.2 | 3610.16 | 1074.06 | 1260.66 | 765.8 | 6.07 | 1.65 | 4.31 | 64.69 | 680 | 5900 | 76.65 | 0.59 | 14.75 | 53.88 | 60 | 9 | 9 | 0.58 | 408 | 413.25 | 268059.59 | 183629.44 | 20230204-164514_fe81d17b-fff4-4284-a53f-54499df1cfb1 | 4.8191
20.58 | 29.11 | 5714.82 | 7.6 | [35.73, 45.79] | [14.99, 9.02] | [8.83, 8.83] | [5.0, 9.09] | 0 | 977.23 | 59.55 | 63.64 | -4.09 | 7.45 | 88.66 | 67 | 19.6 | 8.53 | 15.53 | 5.05 | 5.85 | 3657.49 | 1085.56 | 1251.34 | 769.06 | 6.55 | 1.6 | 4.4 | 62.83 | 680 | 5900 | 77.01 | 0.59 | 15.89 | 51.83 | 60 | 9 | 9 | 0.61 | 408 | 413.46 | 273724.21 | 250862.42 | 20230204-164514_ecad33ea-fca9-4346-a073-2836924fb682 | 1.3049
20.28 | 28.91 | 5732.74 | 7.6 | [43.57, 48.7] | [15.03, 10.08] | [8.92, 8.92] | [9.5, 9.67] | 0 | 1041.13 | 67.52 | 67.7 | -0.18 | 7.49 | 88.83 | 56 | 20.2 | 8.63 | 14.67 | 5.61 | 5.51 | 3668.96 | 1086.82 | 1233.79 | 765.84 | 6.98 | 1.59 | 4.42 | 60.62 | 680 | 5900 | 77.93 | 0.59 | 17.29 | 48.73 | 60 | 9 | 9 | 0.64 | 408 | 413.8 | 326822.4 | 272318.39 | 20230204-164514_9582669a-4c03-4f6e-803b-2f54f7ddb94c | 3.111
20.96 | 29.48 | 5671.91 | 7.59 | [33.3, 52.98] | [14.98, 0.79] | [9.18, 9.18] | [5.0, 10.49] | 0 | 949.48 | 57.46 | 62.95 | -5.49 | 7.44 | 90.07 | 80 | 18.8 | 8.52 | 16.38 | 4.58 | 5.97 | 3630.02 | 1078.92 | 1255.71 | 767.1 | 5.48 | 1.6 | 4.39 | 65.05 | 680 | 5900 | 76.91 | 0.59 | 15.46 | 44.91 | 60 | 9 | 9 | 0.7 | 408 | 414.3 | 271708.17 | 170769.99 | 20230204-164514_51bad202-2151-4da0-b4b0-05344ba1eac0 | 5.7613
21.85 | 30.45 | 5659.47 | 7.6 | [32.17, 47.12] | [15.0, 4.39] | [9.21, 9.21] | [5.0, 9.34] | 0 | 937.07 | 56.38 | 60.72 | -4.34 | 7.43 | 90.22 | 81 | 18.8 | 8.6 | 16.5 | 5.35 | 6.04 | 3622.06 | 1077.07 | 1258.01 | 766.77 | 6.04 | 1.62 | 4.35 | 61.66 | 680 | 5900 | 77.67 | 0.59 | 15.41 | 50.45 | 60 | 9 | 9 | 0.62 | 408 | 413.6 | 270994.44 | 198160.06 | 20230204-164514_79317119-6a13-417d-baf4-283685540ca9 | 4.1572
20.66 | 29.21 | 5724.53 | 7.61 | [35.69, 55.33] | [15.04, 1.36] | [9.06, 9.06] | [5.0, 10.96] | 0 | 973.48 | 59.79 | 65.75 | -5.96 | 7.45 | 89.02 | 64 | 19.6 | 8.56 | 15.16 | 5.5 | 5.88 | 3663.7 | 1087.79 | 1256.65 | 771.3 | 5.46 | 1.62 | 4.37 | 60.86 | 680 | 5900 | 77.23 | 0.59 | 15.82 | 43 | 60 | 9 | 9 | 0.73 | 408 | 414.58 | 274514.63 | 184496.56 | 20230204-164514_6231f9f2-fdd2-4368-a36a-7fc610eaaee7 | 5.138
22.57 | 31.13 | 5635.17 | 7.6 | [46.91, 46.91] | [15.0, 15.0] | [8.87, 8.87] | [5.0, 5.0] | 0 | 1065.68 | 70.78 | 70.78 | 0 | 7.51 | 89.86 | 71 | 21.6 | 8.55 | 17.9 | 4.67 | 5.29 | 3606.51 | 1067.53 | 1204.97 | 750.74 | 14.16 | 1.62 | 4.36 | 64.68 | 680 | 5900 | 77.22 | 0.59 | 18.01 | 94.26 | 60 | 9 | 9 | 0.33 | 408 | 411 | 283605.61 | 283605.61 | 20230204-164514_84e4b75f-319b-4b47-aee6-f7a81f7ba4a6 | 0
22.43 | 31.01 | 5631.5 | 7.59 | [51.97, 69.77] | [15.0, 4.57] | [8.63, 8.63] | [6.46, 13.83] | 0 | 1099.87 | 75.6 | 82.97 | -7.37 | 7.53 | 89.75 | 64 | 22.1 | 8.58 | 17.44 | 4.99 | 5.12 | 3604.16 | 1065.61 | 1192.6 | 747.11 | 5.47 | 1.6 | 4.38 | 63.22 | 680 | 5900 | 77.48 | 0.59 | 18.8 | 34.08 | 60 | 9 | 9 | 0.92 | 408 | 416.3 | 302704.64 | 265225.48 | 20230204-164514_65e59cc7-a64c-4e45-b834-7fef7b1ebdfa | 2.1392
22.21 | 30.69 | 5570.43 | 7.6 | [34.29, 34.29] | [15.0, 15.0] | [8.6, 8.6] | [2.04, 2.04] | 0 | 965.92 | 57.89 | 57.89 | 0 | 7.44 | 90.12 | 70 | 22.2 | 8.49 | 18.33 | 3.88 | 5.77 | 3565.07 | 1058.24 | 1221.6 | 750 | 28.31 | 1.61 | 4.38 | 68.66 | 680 | 5900 | 76.64 | 0.59 | 16.08 | 230.47 | 60 | 9 | 9 | 0.14 | 408 | 409.23 | 242277.96 | 242277.96 | 20230204-164514_839e933d-fbbc-4c9f-a003-fc9a71d216bb | 0
22.15 | 30.69 | 5615.38 | 7.6 | [39.83, 55.85] | [15.01, 1.72] | [8.81, 8.81] | [8.33, 11.06] | 0 | 1013.52 | 63.65 | 66.38 | -2.73 | 7.47 | 90.21 | 62 | 22.4 | 8.54 | 17.44 | 4.71 | 5.54 | 3593.84 | 1065.37 | 1216.76 | 752.29 | 5.75 | 1.62 | 4.37 | 64.44 | 680 | 5900 | 77.09 | 0.59 | 16.98 | 42.6 | 60 | 9 | 9 | 0.74 | 408 | 414.64 | 311278.37 | 190161.97 | 20230204-164514_28f7cf87-bc8a-4553-80e9-80af668123f9 | 6.913
20.72 | 29.26 | 5669.63 | 7.61 | [37.49, 56.89] | [14.98, 1.84] | [8.89, 8.89] | [5.0, 11.27] | 0 | 992.96 | 61.36 | 67.62 | -6.26 | 7.46 | 89.95 | 73 | 18.6 | 8.54 | 15.34 | 5.38 | 5.71 | 3628.56 | 1076.49 | 1236.38 | 761.67 | 5.44 | 1.6 | 4.4 | 61.33 | 680 | 5900 | 77.06 | 0.59 | 16.36 | 41.81 | 60 | 9 | 9 | 0.75 | 408 | 414.76 | 275163.03 | 194705.07 | 20230204-164514_928edafe-f4e8-4d62-828e-81aa9532f232 | 4.5923
22.78 | 31.23 | 5615.41 | 7.6 | [36.36, 55.93] | [15.0, 1.97] | [8.58, 8.58] | [4.54, 11.08] | 0 | 985.87 | 59.94 | 66.48 | -6.54 | 7.45 | 89.86 | 75 | 21.6 | 8.45 | 18.42 | 4.35 | 5.7 | 3593.86 | 1066.05 | 1224.22 | 754.14 | 5.41 | 1.63 | 4.34 | 66 | 680 | 5900 | 76.29 | 0.59 | 16.25 | 42.53 | 60 | 9 | 9 | 0.74 | 408 | 414.65 | 269450.48 | 193263.01 | 20230204-164514_1bb62aef-2a50-423f-abf6-443f25699192 | 4.3486
20.28 | 28.88 | 5729.33 | 7.6 | [44.38, 48.96] | [14.97, 10.11] | [8.98, 8.98] | [10.0, 9.72] | 0 | 1047.23 | 68.33 | 68.05 | 0.28 | 7.5 | 89 | 62 | 19.8 | 8.61 | 15.09 | 5.19 | 5.47 | 3666.77 | 1086.08 | 1231.84 | 765.11 | 7.03 | 1.59 | 4.42 | 62.38 | 680 | 5900 | 77.69 | 0.59 | 17.38 | 48.47 | 60 | 9 | 9 | 0.65 | 408 | 413.83 | 331979.12 | 273548.48 | 20230204-164514_29da8392-1714-45f2-ab56-5cbb3678e7bb | 3.3351
20.66 | 29.14 | 5718.18 | 7.6 | [40.54, 40.54] | [14.96, 14.96] | [9.19, 9.19] | [5.0, 5.0] | 0 | 1015.88 | 64.69 | 64.69 | 0 | 7.48 | 88.99 | 73 | 18.7 | 8.48 | 15.43 | 5.23 | 5.63 | 3659.63 | 1085.24 | 1241.49 | 766.89 | 12.94 | 1.6 | 4.4 | 61.87 | 680 | 5900 | 76.58 | 0.59 | 16.54 | 94.24 | 60 | 9 | 9 | 0.33 | 408 | 411 | 277815.99 | 277815.99 | 20230204-164514_ecc3eece-6e90-44e7-8b84-d5beb58184ad | 0
20.37 | 29.1 | 5712.7 | 7.6 | [44.48, 53.49] | [14.98, 6.58] | [8.89, 8.89] | [10.0, 10.61] | 0 | 1048.85 | 68.35 | 68.96 | -0.61 | 7.5 | 88.94 | 61 | 20 | 8.73 | 15.14 | 5.24 | 5.45 | 3656.13 | 1082.77 | 1227.01 | 762.51 | 6.44 | 1.59 | 4.42 | 62.5 | 680 | 5900 | 78.77 | 0.59 | 17.71 | 44.42 | 60 | 9 | 9 | 0.71 | 408 | 414.37 | 332105.72 | 243182.85 | 20230204-164514_cf1fd2ab-3e79-4f6b-b48d-dd43ca290294 | 5.0755
20.39 | 29.08 | 5722.27 | 7.61 | [43.39, 57.92] | [15.0, 1.95] | [8.97, 8.97] | [10.0, 11.47] | 0 | 1039.64 | 67.36 | 68.84 | -1.48 | 7.49 | 89 | 60 | 20.3 | 8.69 | 15.28 | 5.11 | 5.5 | 3662.25 | 1084.96 | 1232.56 | 764.74 | 5.87 | 1.6 | 4.41 | 62.97 | 680 | 5900 | 78.45 | 0.59 | 17.42 | 41.07 | 60 | 9 | 9 | 0.76 | 408 | 414.88 | 331491.24 | 199074.86 | 20230204-164514_03e995f6-be00-47fc-b141-d6c7b0d0853d | 7.558
20.38 | 29.05 | 5712.01 | 7.59 | [41.95, 56.5] | [15.01, 1.66] | [8.99, 8.99] | [10.0, 11.19] | 0 | 1028.34 | 65.95 | 67.15 | -1.2 | 7.49 | 89.05 | 61 | 20.2 | 8.67 | 15.32 | 5.06 | 5.55 | 3655.69 | 1083.4 | 1234.16 | 764.39 | 5.89 | 1.59 | 4.42 | 63.13 | 680 | 5900 | 78.23 | 0.59 | 17.18 | 42.11 | 60 | 9 | 9 | 0.75 | 408 | 414.71 | 330346.6 | 191409.6 | 20230204-164514_2d60ad7c-07a6-48ce-96e6-3ff78d1a2c11 | 7.9302
20.73 | 29.24 | 5680.9 | 7.6 | [36.96, 56.38] | [14.88, 1.63] | [8.99, 8.99] | [5.0, 11.17] | 0 | 988.53 | 60.83 | 67 | -6.17 | 7.46 | 90.02 | 73 | 19.2 | 8.51 | 15.9 | 4.82 | 5.75 | 3635.78 | 1078.98 | 1241.83 | 764.06 | 5.45 | 1.6 | 4.4 | 63.82 | 680 | 5900 | 76.82 | 0.59 | 16.18 | 42.19 | 60 | 9 | 9 | 0.74 | 408 | 414.7 | 273577.92 | 190799.23 | 20230204-164514_54499e68-c359-44e9-b68f-c5bad4740bc1 | 4.7248
20.64 | 29.16 | 5689.67 | 7.6 | [24.91, 40.34] | [15.1, 2.66] | [8.97, 8.97] | [5.0, 8.0] | 0 | 849.14 | 48.98 | 51.97 | -2.99 | 7.37 | 89.8 | 74 | 18.4 | 8.52 | 15.27 | 5.36 | 6.7 | 3641.39 | 1086.29 | 1300.28 | 780.06 | 6.13 | 1.62 | 4.36 | 61.37 | 680 | 5900 | 76.94 | 0.59 | 13.5 | 58.94 | 60 | 9 | 9 | 0.53 | 408 | 412.8 | 265609.97 | 157091.77 | 20230204-164514_45475a7f-7574-4140-a1de-b440ed5bd7a0 | 6.194
20.95 | 29.44 | 5671.27 | 7.59 | [37.8, 57.2] | [15.0, 1.93] | [8.86, 8.86] | [5.0, 11.33] | 0 | 995.7 | 61.66 | 67.99 | -6.33 | 7.46 | 89.96 | 82 | 18.4 | 8.48 | 16.23 | 4.72 | 5.7 | 3629.62 | 1076.65 | 1235.41 | 761.52 | 5.44 | 1.59 | 4.41 | 64.25 | 680 | 5900 | 76.58 | 0.59 | 16.31 | 41.59 | 60 | 9 | 9 | 0.76 | 408 | 414.8 | 275620.52 | 196672.47 | 20230204-164514_1ddf0bb0-56b9-41f4-9bda-3dac288c62de | 4.5062
20.24 | 28.86 | 5739.89 | 7.6 | [36.64, 36.64] | [14.99, 14.99] | [9.01, 9.01] | [6.36, 6.36] | 0 | 983.81 | 60.64 | 60.64 | 0 | 7.46 | 89.09 | 62 | 19.6 | 8.61 | 14.9 | 5.34 | 5.83 | 3673.53 | 1090.3 | 1256.04 | 772.32 | 9.54 | 1.6 | 4.4 | 61.72 | 680 | 5900 | 77.74 | 0.59 | 16.08 | 74.13 | 60 | 9 | 9 | 0.42 | 408 | 411.81 | 288380.93 | 288380.93 | 20230204-164514_a5249d55-0fac-457b-9e58-f6215028f2e2 | 0
22.45 | 30.91 | 5594.83 | 7.6 | [34.03, 55.55] | [15.0, 1.49] | [8.98, 8.98] | [2.99, 11.0] | 0 | 958.87 | 58.01 | 66.02 | -8.01 | 7.44 | 90.04 | 73 | 22.1 | 8.46 | 18.63 | 3.82 | 5.83 | 3580.69 | 1063.63 | 1233.1 | 755.1 | 5.27 | 1.63 | 4.35 | 68.91 | 680 | 5900 | 76.36 | 0.59 | 15.79 | 42.83 | 60 | 9 | 9 | 0.73 | 408 | 414.6 | 252028.35 | 186552.73 | 20230204-164514_25da6688-3873-4b27-bcba-db7d4f61ebb0 | 3.7372
22.06 | 30.56 | 5561.58 | 7.6 | [41.09, 41.09] | [15.06, 15.06] | [8.75, 8.75] | [4.18, 4.18] | 0 | 1023.55 | 64.9 | 64.9 | 0 | 7.48 | 90.08 | 68 | 22.1 | 8.51 | 17.97 | 4.08 | 5.43 | 3559.41 | 1054.74 | 1201.11 | 743.99 | 15.51 | 1.6 | 4.4 | 67.57 | 680 | 5900 | 76.79 | 0.59 | 17.32 | 112.63 | 60 | 9 | 9 | 0.28 | 408 | 410.51 | 270919.06 | 270919.06 | 20230204-164514_4fe29a84-02e9-4731-8a3f-8b8a9cd627a9 | 0
20.4 | 29.22 | 5621.1 | 7.6 | [50.95, 65.25] | [20.27, 8.88] | [10.01, 10.01] | [10.04, 12.94] | 0 | 1011.63 | 81.23 | 84.14 | -2.91 | 7.45 | 88.85 | 52 | 21 | 8.81 | 14.83 | 5.57 | 5.56 | 3597.5 | 1064.89 | 1206.74 | 749.41 | 6.28 | 1.57 | 4.45 | 61.28 | 680 | 5900 | 79.56 | 0.59 | 17.46 | 36.41 | 60 | 9 | 9 | 0.86 | 408 | 415.77 | 403988.54 | 306315.89 | 20230204-165137_c295c30f-170f-446e-93cd-7100bdc267ab | 5.5749
20.45 | 29.29 | 5651.42 | 7.61 | [36.27, 39.66] | [20.01, 14.52] | [8.97, 8.97] | [10.0, 7.89] | 0 | 907.96 | 65.25 | 63.15 | 2.1 | 7.37 | 89 | 67 | 19.4 | 8.84 | 15.35 | 5.1 | 6.22 | 3616.91 | 1072.82 | 1239.58 | 759.67 | 8.27 | 1.6 | 4.41 | 63.4 | 680 | 5900 | 79.8 | 0.59 | 15.27 | 59.7 | 60 | 9 | 9 | 0.53 | 408 | 412.74 | 386670.56 | 300831.08 | 20230204-165137_80245d9c-ca9b-4b15-90d8-d1451956c24a | 4.8995
20.4 | 29.22 | 5621.1 | 7.6 | [50.95, 71.86] | [20.27, 3.56] | [10.01, 10.01] | [10.04, 14.24] | 0 | 1011.63 | 81.23 | 85.43 | -4.2 | 7.45 | 88.85 | 58 | 20.8 | 8.81 | 15.46 | 4.94 | 5.56 | 3597.5 | 1064.89 | 1206.74 | 749.41 | 5.71 | 1.57 | 4.45 | 64.09 | 680 | 5900 | 79.56 | 0.59 | 17.46 | 33.1 | 60 | 9 | 9 | 0.95 | 408 | 416.54 | 403988.54 | 260041.28 | 20230204-165137_9621d0bf-4c6a-46cc-8757-cb5eb4044f98 | 8.2162
20.36 | 29.16 | 5705.99 | 7.6 | [42.8, 47.61] | [15.01, 9.65] | [8.91, 8.91] | [10.0, 9.45] | 0 | 1035.86 | 66.72 | 66.17 | 0.55 | 7.49 | 89 | 63 | 19.9 | 8.8 | 15.3 | 5.06 | 5.51 | 3651.83 | 1081.93 | 1229.8 | 762.74 | 7.06 | 1.59 | 4.42 | 63.49 | 680 | 5900 | 79.42 | 0.59 | 17.62 | 49.85 | 60 | 9 | 9 | 0.63 | 408 | 413.67 | 330970.19 | 263965.05 | 20230204-165137_1c14ce1a-dfc5-4646-8807-d96978ce9869 | 3.8245
20.46 | 29.22 | 5654.4 | 7.6 | [37.71, 57.16] | [19.96, 1.83] | [8.95, 8.95] | [10.0, 11.32] | 0 | 922.51 | 66.62 | 67.94 | -1.32 | 7.38 | 88.91 | 65 | 20.1 | 8.77 | 15.74 | 4.72 | 6.13 | 3618.82 | 1072.91 | 1235.18 | 758.79 | 5.88 | 1.59 | 4.42 | 65.01 | 680 | 5900 | 79.13 | 0.59 | 15.43 | 41.62 | 60 | 9 | 9 | 0.75 | 408 | 414.79 | 387314.88 | 195453.13 | 20230204-165137_f89eb99b-363b-4019-9653-0829b3735acf | 10.951
20.38 | 29.1 | 5573.63 | 7.6 | [37.54, 50.54] | [20.02, 7.05] | [7.59, 7.59] | [10.0, 10.03] | 0 | 933.02 | 65.15 | 65.18 | -0.03 | 7.36 | 89.07 | 63 | 20.4 | 8.72 | 15.76 | 4.63 | 5.97 | 3567.12 | 1055.51 | 1201.37 | 743.01 | 6.5 | 1.57 | 4.46 | 65.33 | 680 | 5900 | 78.7 | 0.59 | 15.82 | 47 | 60 | 9 | 9 | 0.67 | 408 | 414.02 | 386678.79 | 239233.76 | 20230204-165137_d633fee3-c775-453b-99c0-6054e444eeec | 8.4158
20.47 | 29.24 | 5708.32 | 7.6 | [32.95, 50.99] | [18.64, 0.7] | [8.9, 8.9] | [10.0, 10.1] | 0 | 893.79 | 60.49 | 60.59 | -0.1 | 7.37 | 89.15 | 74 | 19 | 8.76 | 15.84 | 4.63 | 6.39 | 3653.32 | 1084.89 | 1262.93 | 770.45 | 5.99 | 1.61 | 4.39 | 65.42 | 680 | 5900 | 79.12 | 0.59 | 14.69 | 46.67 | 60 | 9 | 9 | 0.67 | 408 | 414.06 | 366854.93 | 163610.58 | 20230204-165137_ad972651-7591-4bd0-a4fa-91be4000cca2 | 11.6007
20.05 | 28.54 | 5561.52 | 7.6 | [34.97, 51.9] | [19.95, 3.32] | [6.5, 6.5] | [10.0, 10.29] | 0 | 919.95 | 61.42 | 61.72 | -0.3 | 7.33 | 89.14 | 65 | 19.5 | 8.49 | 15.19 | 4.85 | 6.05 | 3559.38 | 1052.06 | 1191.73 | 738.84 | 5.97 | 1.56 | 4.48 | 63.63 | 680 | 5900 | 76.68 | 0.59 | 15.2 | 45.82 | 60 | 9 | 9 | 0.69 | 408 | 414.17 | 382624.68 | 196334.5 | 20230204-165137_95364b8d-c523-4e87-b884-1cae28969ae8 | 10.633
20 | 28.53 | 5540.97 | 7.59 | [42.09, 45.36] | [20.0, 15.75] | [6.58, 6.58] | [10.0, 9.03] | 0 | 982.82 | 68.67 | 67.69 | 0.98 | 7.38 | 88.96 | 62 | 20.3 | 8.52 | 15.54 | 4.47 | 5.64 | 3546.22 | 1046.93 | 1171.97 | 732.54 | 7.61 | 1.54 | 4.51 | 65.61 | 680 | 5900 | 76.93 | 0.59 | 16.59 | 52.21 | 60 | 9 | 9 | 0.6 | 408 | 413.42 | 389574.23 | 330376.04 | 20230204-165137_8604d278-3aad-43ea-bda4-86f580182269 | 3.3789
20.04 | 28.57 | 5568.82 | 7.6 | [41.31, 48.57] | [20.03, 12.42] | [6.57, 6.57] | [10.0, 9.65] | 0 | 976.18 | 67.91 | 67.56 | 0.35 | 7.38 | 89.01 | 61 | 20.4 | 8.53 | 15.5 | 4.54 | 5.7 | 3564.05 | 1052.3 | 1179.31 | 736.55 | 7.04 | 1.56 | 4.49 | 65.27 | 680 | 5900 | 77.01 | 0.59 | 16.37 | 48.83 | 60 | 9 | 9 | 0.64 | 408 | 413.79 | 389144.79 | 298684.03 | 20230204-165137_61379513-1a10-45da-a506-17b1d58992b0 | 5.1633
20.12 | 28.71 | 5571.31 | 7.6 | [39.25, 43.16] | [19.96, 14.63] | [6.61, 6.61] | [10.0, 8.59] | 0 | 958.97 | 65.82 | 64.4 | 1.42 | 7.37 | 88.93 | 60 | 20.4 | 8.59 | 15.37 | 4.75 | 5.81 | 3565.64 | 1053.21 | 1184.68 | 738.07 | 7.66 | 1.56 | 4.48 | 64.4 | 680 | 5900 | 77.56 | 0.59 | 16.13 | 54.88 | 60 | 9 | 9 | 0.57 | 408 | 413.15 | 386660.96 | 310298.04 | 20230204-165137_1ad3bebf-ae09-44ab-ae51-d0dd3b712525 | 4.3586
20.47 | 29.23 | 5641.03 | 7.6 | [37.9, 52.01] | [20.01, 6.21] | [8.83, 8.83] | [10.0, 10.32] | 0 | 924.7 | 66.74 | 67.05 | -0.31 | 7.38 | 89.03 | 63 | 20.3 | 8.76 | 15.67 | 4.8 | 6.1 | 3610.26 | 1070.13 | 1230.28 | 756.41 | 6.47 | 1.58 | 4.43 | 64.59 | 680 | 5900 | 79.08 | 0.59 | 15.5 | 45.68 | 60 | 9 | 9 | 0.69 | 408 | 414.19 | 387910.13 | 234278.3 | 20230204-165137_ed6c7eee-d2e2-4d7a-93ee-5165566a2390 | 8.7689
20.37 | 29.18 | 5630.43 | 7.59 | [38.85, 52.95] | [19.97, 6.37] | [8.94, 8.94] | [10.0, 10.5] | 0 | 932.87 | 67.76 | 68.26 | -0.5 | 7.38 | 88.95 | 61 | 20.6 | 8.81 | 15.68 | 4.69 | 6.04 | 3603.47 | 1068.03 | 1226.43 | 754.68 | 6.45 | 1.58 | 4.44 | 65.27 | 680 | 5900 | 79.55 | 0.59 | 15.8 | 44.87 | 60 | 9 | 9 | 0.7 | 408 | 414.3 | 388360.26 | 239059.48 | 20230204-165137_b3c632c6-212c-4083-9a0a-b35a3a3f3f9d | 8.5217
20.35 | 29.06 | 5709.88 | 7.61 | [42.89, 43.93] | [15.01, 12.7] | [8.87, 8.87] | [10.0, 8.73] | 0 | 1036.81 | 66.77 | 65.5 | 1.27 | 7.49 | 89.04 | 67 | 19.4 | 8.7 | 15.35 | 5 | 5.51 | 3654.32 | 1082.59 | 1230 | 763.07 | 7.64 | 1.6 | 4.41 | 63.5 | 680 | 5900 | 78.58 | 0.59 | 17.43 | 53.95 | 60 | 9 | 9 | 0.58 | 408 | 413.24 | 331099.36 | 290788.57 | 20230204-165137_cff838f3-6e5d-4516-81e5-19207da7ac79 | 2.3008
20.47 | 29.24 | 5618.03 | 7.6 | [35.37, 38.87] | [20.01, 14.24] | [8.78, 8.78] | [10.0, 7.74] | 0 | 900.95 | 64.16 | 61.89 | 2.27 | 7.36 | 89.15 | 68 | 19.5 | 8.77 | 15.57 | 4.9 | 6.24 | 3595.54 | 1066.45 | 1232.87 | 755.21 | 8.29 | 1.59 | 4.42 | 64.16 | 680 | 5900 | 79.2 | 0.59 | 15.13 | 60.91 | 60 | 9 | 9 | 0.52 | 408 | 412.64 | 385747.04 | 295029.95 | 20230204-165137_348859cd-0c7c-4d38-8271-ee07aa4de376 | 5.1779
20.56 | 29.33 | 5674.13 | 7.6 | [33.43, 52.89] | [20.0, 1.01] | [8.95, 8.95] | [10.0, 10.47] | 0 | 879.58 | 62.38 | 62.85 | -0.47 | 7.35 | 89.19 | 73 | 19.2 | 8.76 | 15.9 | 4.66 | 6.45 | 3631.44 | 1078.08 | 1254.79 | 765.29 | 5.95 | 1.6 | 4.4 | 65.28 | 680 | 5900 | 79.11 | 0.59 | 14.51 | 44.99 | 60 | 9 | 9 | 0.7 | 408 | 414.28 | 383950.55 | 172993.82 | 20230204-165137_aa322059-dd48-4ba5-b2f9-185ff55262df | 12.0409
20.4 | 29.24 | 5622.33 | 7.6 | [41.93, 51.56] | [20.08, 10.68] | [9.43, 9.43] | [10.01, 10.24] | 0 | 953.41 | 71.44 | 71.67 | -0.23 | 7.4 | 88.79 | 65 | 19.8 | 8.84 | 15.47 | 4.93 | 5.9 | 3598.29 | 1066.36 | 1221.61 | 753.07 | 6.98 | 1.59 | 4.43 | 64.17 | 680 | 5900 | 79.78 | 0.59 | 16.29 | 46.03 | 60 | 9 | 9 | 0.68 | 408 | 414.14 | 392885.77 | 288473.17 | 20230204-165137_1f05bf9e-1871-439a-bc77-80884210212d | 5.9596
20.24 | 28.74 | 5556.92 | 7.6 | [38.63, 46.4] | [20.13, 11.58] | [6.55, 6.55] | [10.0, 9.22] | 0 | 951.69 | 65.31 | 64.53 | 0.78 | 7.36 | 89.05 | 66 | 19.6 | 8.5 | 15.41 | 4.84 | 5.84 | 3556.43 | 1050.49 | 1182.38 | 736.25 | 7.08 | 1.56 | 4.48 | 63.73 | 680 | 5900 | 76.71 | 0.59 | 15.85 | 51.11 | 60 | 9 | 9 | 0.61 | 408 | 413.53 | 388149.03 | 282136.73 | 20230204-165137_cbcf051a-c141-4f24-afb4-f24ce0d0a08b | 6.0509
20.6 | 29.36 | 5666.06 | 7.6 | [36.47, 56.0] | [20.02, 1.58] | [8.97, 8.97] | [10.0, 11.09] | 0 | 909.82 | 65.46 | 66.55 | -1.09 | 7.37 | 88.97 | 73 | 18.8 | 8.76 | 15.53 | 5.07 | 6.23 | 3626.28 | 1075.53 | 1242.11 | 761.46 | 5.9 | 1.6 | 4.41 | 63.33 | 680 | 5900 | 79.06 | 0.59 | 15.12 | 42.49 | 60 | 9 | 9 | 0.74 | 408 | 414.65 | 386989.43 | 189047.82 | 20230204-165137_47ea079d-c421-401e-a746-50893cfefd28 | 11.298
20.55 | 29.32 | 5684.77 | 7.59 | [40.85, 60.2] | [19.97, 2.55] | [8.81, 8.81] | [10.0, 11.93] | 0 | 951.5 | 69.63 | 71.56 | -1.93 | 7.4 | 88.82 | 62 | 20.1 | 8.77 | 15.36 | 5.19 | 5.97 | 3638.25 | 1077.61 | 1231.05 | 760.07 | 5.84 | 1.59 | 4.42 | 62.82 | 680 | 5900 | 79.18 | 0.59 | 15.92 | 39.51 | 60 | 9 | 9 | 0.8 | 408 | 415.16 | 390015.5 | 212871.74 | 20230204-165137_600053d1-8ec0-4598-8a05-325750e6c84b | 10.1109
20.18 | 28.66 | 5566.29 | 7.59 | [38.8, 46.49] | [20.04, 11.6] | [6.57, 6.57] | [10.0, 9.24] | 0 | 954.35 | 65.41 | 64.66 | 0.75 | 7.36 | 88.88 | 64 | 19.8 | 8.48 | 15.34 | 4.84 | 5.83 | 3562.42 | 1052.27 | 1184.17 | 737.49 | 7.08 | 1.55 | 4.49 | 63.67 | 680 | 5900 | 76.57 | 0.59 | 15.85 | 51.02 | 60 | 9 | 9 | 0.62 | 408 | 413.54 | 387142.22 | 282589.05 | 20230204-165137_51dfde6a-b18d-4e17-b0ae-86defcc16b18 | 5.9676
20.4 | 29.22 | 5621.1 | 7.6 | [50.95, 65.25] | [20.27, 8.88] | [10.01, 10.01] | [10.04, 12.94] | 0 | 1011.63 | 81.23 | 84.14 | -2.91 | 7.45 | 88.85 | 57 | 20.3 | 8.81 | 14.89 | 5.52 | 5.56 | 3597.5 | 1064.89 | 1206.74 | 749.41 | 6.28 | 1.57 | 4.45 | 61.51 | 680 | 5900 | 79.56 | 0.59 | 17.46 | 36.41 | 60 | 9 | 9 | 0.86 | 408 | 415.77 | 403988.54 | 306315.89 | 20230204-165137_64528c0b-c434-498c-ba96-3fe28a466488 | 5.5749
20.15 | 29.05 | 5572.64 | 7.6 | [40.43, 49.91] | [19.91, 10.36] | [9.1, 9.1] | [9.99, 9.91] | 0 | 945.98 | 69.44 | 69.37 | 0.07 | 7.4 | 88.96 | 55 | 20.9 | 8.91 | 15.15 | 4.99 | 5.89 | 3566.49 | 1056.89 | 1211.19 | 746.38 | 7.01 | 1.57 | 4.46 | 64.08 | 680 | 5900 | 80.4 | 0.59 | 16.44 | 47.55 | 60 | 9 | 9 | 0.66 | 408 | 413.95 | 389059.1 | 279481.38 | 20230204-165137_e48cf637-8546-40cf-8686-cc24dc108b34 | 6.2544
20.01 | 28.59 | 5551.81 | 7.61 | [38.78, 55.89] | [20.0, 3.97] | [6.61, 6.61] | [10.0, 11.08] | 0 | 954.3 | 65.39 | 66.47 | -1.08 | 7.36 | 88.94 | 63 | 19.8 | 8.58 | 15.21 | 4.8 | 5.82 | 3553.16 | 1049.6 | 1181.55 | 735.72 | 5.9 | 1.56 | 4.48 | 64.14 | 680 | 5900 | 77.46 | 0.59 | 16.08 | 42.54 | 60 | 9 | 9 | 0.74 | 408 | 414.65 | 386708.09 | 215963.57 | 20230204-165137_6103b2d8-87eb-43a1-861e-f31ce45dd85e | 9.7457
20.08 | 28.55 | 5562.73 | 7.6 | [42.06, 59.35] | [20.1, 4.57] | [6.66, 6.66] | [10.0, 11.76] | 0 | 980.48 | 68.82 | 70.58 | -1.76 | 7.38 | 88.9 | 60 | 20.1 | 8.47 | 15.1 | 4.98 | 5.67 | 3560.15 | 1051.15 | 1177.6 | 735.7 | 5.85 | 1.55 | 4.49 | 62.98 | 680 | 5900 | 76.49 | 0.59 | 16.37 | 40.06 | 60 | 9 | 9 | 0.78 | 408 | 415.06 | 390747.23 | 233431.12 | 20230204-165137_ce5974f5-1ab8-43a8-9cf0-58cb35b8613a | 8.9792
20.43 | 29.15 | 5706.09 | 7.6 | [40.73, 42.39] | [14.93, 11.7] | [9.11, 9.11] | [10.0, 8.43] | 0 | 1018.67 | 64.77 | 63.2 | 1.57 | 7.48 | 89.07 | 72 | 18.8 | 8.72 | 15.41 | 5.03 | 5.6 | 3651.9 | 1082.79 | 1237.44 | 764.87 | 7.69 | 1.59 | 4.41 | 63.43 | 680 | 5900 | 78.68 | 0.59 | 17.1 | 55.93 | 60 | 9 | 9 | 0.56 | 408 | 413.06 | 328354.68 | 274163.11 | 20230204-165137_701f1cfc-208c-4cf1-bce0-1049c6a0ea13 | 3.0931
20.06 | 28.59 | 5520.47 | 7.6 | [38.63, 55.7] | [20.0, 3.98] | [6.56, 6.56] | [10.0, 11.04] | 0 | 953.42 | 65.19 | 66.24 | -1.05 | 7.36 | 89.03 | 64 | 20.5 | 8.53 | 15.98 | 4.09 | 5.79 | 3533.1 | 1043.63 | 1174.68 | 731.48 | 5.91 | 1.55 | 4.5 | 67.6 | 680 | 5900 | 76.96 | 0.59 | 16.07 | 42.69 | 60 | 9 | 9 | 0.74 | 408 | 414.62 | 386564.42 | 215466.45 | 20230204-165802_af3c21dd-bf35-48d1-8638-df86aa5dfe04 | 9.7659
20.26 | 28.78 | 5519.83 | 7.6 | [38.18, 55.31] | [20.01, 3.83] | [6.63, 6.63] | [10.0, 10.96] | 0 | 948.49 | 64.82 | 65.77 | -0.95 | 7.36 | 88.93 | 66 | 20.1 | 8.53 | 15.87 | 4.39 | 5.82 | 3532.69 | 1043.71 | 1176.45 | 731.9 | 5.91 | 1.56 | 4.49 | 66.02 | 680 | 5900 | 76.97 | 0.59 | 15.97 | 42.98 | 60 | 9 | 9 | 0.73 | 408 | 414.58 | 386325.83 | 212652.31 | 20230204-165802_882cfc9b-5391-4bb1-9670-8bf01bddd76b | 9.9129
19.96 | 28.51 | 5523.98 | 7.6 | [39.26, 56.57] | [20.09, 3.99] | [6.72, 6.72] | [10.0, 11.21] | 0 | 956.3 | 66.07 | 67.28 | -1.21 | 7.36 | 88.97 | 61 | 20.5 | 8.54 | 15.59 | 4.37 | 5.78 | 3535.35 | 1044.4 | 1175.91 | 732.16 | 5.89 | 1.55 | 4.5 | 66.15 | 680 | 5900 | 77.14 | 0.59 | 16.15 | 42.03 | 60 | 9 | 9 | 0.75 | 408 | 414.73 | 388220.22 | 218262.88 | 20230204-165802_1a0064e4-d9c3-491e-a096-ef05933c299f | 9.7008
20.49 | 29.01 | 5498.35 | 7.6 | [43.19, 46.38] | [20.02, 16.19] | [6.64, 6.64] | [9.88, 9.23] | 0 | 990.68 | 69.85 | 69.21 | 0.64 | 7.39 | 88.83 | 70 | 20.3 | 8.52 | 16.56 | 3.93 | 5.55 | 3518.94 | 1038.79 | 1161.59 | 726.62 | 7.57 | 1.55 | 4.5 | 68.44 | 680 | 5900 | 76.93 | 0.59 | 16.91 | 51.07 | 60 | 9 | 9 | 0.62 | 408 | 413.54 | 389622.04 | 338747.52 | 20230204-165802_2d2cd15a-700d-48b2-af08-4b6af76811f8 | 2.9038
20.81 | 29.36 | 5481.37 | 7.6 | [36.49, 53.9] | [19.96, 3.5] | [6.7, 6.7] | [9.73, 10.68] | 0 | 932.78 | 63.15 | 64.1 | -0.95 | 7.35 | 89.17 | 73 | 20.1 | 8.55 | 16.75 | 4.06 | 5.88 | 3508.08 | 1036.89 | 1173.16 | 728.04 | 5.91 | 1.56 | 4.47 | 67.82 | 680 | 5900 | 77.17 | 0.59 | 15.83 | 44.11 | 60 | 9 | 9 | 0.71 | 408 | 414.41 | 381418.81 | 204501.21 | 20230204-165802_632d1e26-5042-464a-8260-eedaac13669f | 10.098
19.91 | 28.41 | 5530.56 | 7.6 | [38.4, 50.31] | [19.9, 7.97] | [6.61, 6.61] | [10.0, 9.98] | 0 | 952.25 | 64.91 | 64.89 | 0.02 | 7.36 | 89 | 61 | 20.4 | 8.51 | 15.5 | 4.41 | 5.81 | 3539.56 | 1045.67 | 1177.91 | 733.14 | 6.5 | 1.55 | 4.5 | 65.88 | 680 | 5900 | 76.8 | 0.59 | 15.97 | 47.2 | 60 | 9 | 9 | 0.67 | 408 | 413.99 | 385162.64 | 249105.74 | 20230204-165802_4afa75e7-47bc-470d-8b86-0bc9a5050d57 | 7.7658
21.15 | 29.68 | 5470.95 | 7.6 | [34.58, 52.78] | [20.03, 3.49] | [6.49, 6.49] | [8.8, 10.46] | 0 | 914.93 | 61.1 | 62.76 | -1.66 | 7.33 | 89.1 | 79 | 19.4 | 8.52 | 16.83 | 4.32 | 5.98 | 3501.41 | 1035 | 1173.35 | 727.03 | 5.84 | 1.57 | 4.46 | 66.35 | 680 | 5900 | 76.94 | 0.59 | 15.45 | 45.05 | 60 | 9 | 9 | 0.7 | 408 | 414.28 | 371030.5 | 201010.51 | 20230204-165802_20f46fb5-c188-4943-95dc-6439ebb32ff6 | 9.7043
21.31 | 29.91 | 5470.14 | 7.6 | [35.9, 55.62] | [19.96, 3.3] | [7.21, 7.21] | [7.96, 11.02] | 0 | 921.88 | 63.07 | 66.13 | -3.06 | 7.35 | 88.83 | 71 | 21 | 8.6 | 17.34 | 3.97 | 5.93 | 3500.89 | 1035.72 | 1178.84 | 728.89 | 5.72 | 1.57 | 4.46 | 68.45 | 680 | 5900 | 77.67 | 0.59 | 15.74 | 42.75 | 60 | 9 | 9 | 0.73 | 408 | 414.61 | 363523.01 | 207537.2 | 20230204-165802_1e69a806-01af-404d-8d27-3dcb8095113f | 8.9033
20.23 | 28.75 | 5516 | 7.6 | [37.16, 54.2] | [19.99, 3.68] | [6.57, 6.57] | [10.0, 10.74] | 0 | 940.08 | 63.72 | 64.45 | -0.73 | 7.35 | 89.04 | 67 | 20.1 | 8.52 | 15.99 | 4.24 | 5.87 | 3530.24 | 1043.09 | 1177.25 | 731.73 | 5.93 | 1.55 | 4.49 | 66.76 | 680 | 5900 | 76.87 | 0.59 | 15.79 | 43.87 | 60 | 9 | 9 | 0.72 | 408 | 414.45 | 385015.31 | 207580.73 | 20230204-165802_cb700177-30e7-4a4a-a460-a92cdad547b6 | 10.1275
20.59 | 29.17 | 5492.93 | 7.6 | [34.76, 52.07] | [19.98, 3.09] | [6.75, 6.75] | [9.9, 10.32] | 0 | 914.73 | 61.49 | 61.91 | -0.42 | 7.33 | 89.11 | 78 | 19.1 | 8.58 | 16.42 | 4.17 | 6 | 3515.48 | 1039.56 | 1181.06 | 730.9 | 5.96 | 1.56 | 4.48 | 67.3 | 680 | 5900 | 77.44 | 0.59 | 15.47 | 45.67 | 60 | 9 | 9 | 0.69 | 408 | 414.19 | 382009.14 | 194254.24 | 20230204-165802_f84c5deb-0886-43dd-a481-fa2d80c75aca | 10.7166
20.53 | 29.13 | 5500.96 | 7.6 | [34.02, 50.98] | [19.99, 3.28] | [6.36, 6.36] | [9.86, 10.1] | 0 | 911.11 | 60.37 | 60.62 | -0.25 | 7.32 | 88.97 | 74 | 19.7 | 8.6 | 16.5 | 4.03 | 6.04 | 3520.62 | 1040.58 | 1179.55 | 730.85 | 5.98 | 1.56 | 4.48 | 68.12 | 680 | 5900 | 77.66 | 0.59 | 15.42 | 46.65 | 60 | 9 | 9 | 0.67 | 408 | 414.06 | 380695.13 | 193095.97 | 20230204-165802_68e7c892-cc79-4328-8501-4e2634f2ca75 | 10.7077
19.92 | 28.45 | 5531.85 | 7.6 | [38.32, 39.33] | [20.0, 16.83] | [6.52, 6.52] | [10.0, 7.83] | 0 | 951.1 | 64.84 | 62.68 | 2.16 | 7.36 | 89.07 | 58 | 20.4 | 8.53 | 15.11 | 4.81 | 5.82 | 3540.38 | 1045.78 | 1177.31 | 733.01 | 8.28 | 1.55 | 4.5 | 63.96 | 680 | 5900 | 77.03 | 0.59 | 15.99 | 60.15 | 60 | 9 | 9 | 0.52 | 408 | 412.7 | 386148.95 | 326125.18 | 20230204-165802_3d66bad6-2018-4905-9424-37488e30796c | 3.426
20.97 | 29.45 | 5479.57 | 7.6 | [38.39, 43.19] | [19.96, 14.56] | [6.69, 6.69] | [9.18, 8.59] | 0 | 950.49 | 65.04 | 64.44 | 0.6 | 7.36 | 89.02 | 81 | 19.8 | 8.47 | 17.46 | 3.51 | 5.76 | 3506.93 | 1036.15 | 1168.07 | 726.67 | 7.57 | 1.57 | 4.47 | 70.69 | 680 | 5900 | 76.49 | 0.59 | 16.05 | 54.84 | 60 | 9 | 9 | 0.57 | 408 | 413.16 | 377640.99 | 309640.22 | 20230204-165802_feb252c6-3db4-4791-9927-619e2f709f0e | 3.8813
21.19 | 29.66 | 5474.08 | 7.6 | [31.1, 49.76] | [19.97, 2.78] | [6.62, 6.62] | [8.38, 9.86] | 0 | 876.76 | 57.69 | 59.16 | -1.47 | 7.3 | 89.08 | 80 | 20 | 8.48 | 17.53 | 3.66 | 6.24 | 3503.41 | 1036.72 | 1186.49 | 730.53 | 5.85 | 1.57 | 4.46 | 69.87 | 680 | 5900 | 76.54 | 0.59 | 14.6 | 47.79 | 60 | 9 | 9 | 0.66 | 408 | 413.92 | 363133.97 | 183711.49 | 20230204-165802_70d42718-9c30-4d4f-ad14-5027e8a36bf3 | 10.241
20.5 | 29.02 | 5507.02 | 7.6 | [32.97, 50.03] | [19.91, 2.78] | [6.68, 6.68] | [10.0, 9.91] | 0 | 897.82 | 59.56 | 59.49 | 0.07 | 7.32 | 89.09 | 77 | 19.6 | 8.52 | 16.78 | 3.72 | 6.13 | 3524.5 | 1042.55 | 1188.29 | 733.73 | 6.01 | 1.56 | 4.48 | 69.61 | 680 | 5900 | 76.91 | 0.59 | 14.98 | 47.54 | 60 | 9 | 9 | 0.66 | 408 | 413.95 | 380542.56 | 184435.75 | 20230204-165802_4f0cadb0-e4dd-469a-98ec-db4abdf80a2a | 11.1933
20.34 | 28.86 | 5509.08 | 7.6 | [41.03, 58.32] | [20.04, 4.31] | [6.72, 6.72] | [10.0, 11.56] | 0 | 972.18 | 67.79 | 69.35 | -1.56 | 7.38 | 89 | 68 | 20.2 | 8.52 | 16.21 | 4.12 | 5.67 | 3525.81 | 1041.28 | 1168.95 | 729.3 | 5.87 | 1.55 | 4.5 | 67.4 | 680 | 5900 | 76.94 | 0.59 | 16.49 | 40.77 | 60 | 9 | 9 | 0.77 | 408 | 414.94 | 389217.48 | 227352.06 | 20230204-165802_046f84fc-1da3-4660-84d7-121831a90fdd | 9.2389
20.76 | 29.28 | 5497.07 | 7.6 | [39.03, 56.69] | [19.98, 4.19] | [6.54, 6.54] | [9.37, 11.24] | 0 | 957.46 | 65.55 | 67.42 | -1.87 | 7.36 | 88.8 | 80 | 19.2 | 8.52 | 16.76 | 3.99 | 5.74 | 3518.12 | 1039.11 | 1168.56 | 728.1 | 5.83 | 1.56 | 4.48 | 68.09 | 680 | 5900 | 76.95 | 0.59 | 16.23 | 41.94 | 60 | 9 | 9 | 0.75 | 408 | 414.74 | 380191.24 | 220902.32 | 20230204-165802_48dbed83-c165-48f4-b25c-bc3300aa41a1 | 9.0918
20.72 | 29.28 | 5499.02 | 7.6 | [28.93, 46.71] | [20.02, 2.14] | [6.68, 6.68] | [9.36, 9.25] | 0 | 849.39 | 55.63 | 55.53 | 0.1 | 7.28 | 89.05 | 87 | 18.6 | 8.56 | 17.03 | 3.69 | 6.47 | 3519.38 | 1042.22 | 1200.91 | 736.04 | 6.01 | 1.57 | 4.46 | 69.86 | 680 | 5900 | 77.27 | 0.59 | 14.12 | 50.92 | 60 | 9 | 9 | 0.62 | 408 | 413.55 | 371843.33 | 167015.55 | 20230204-165802_2c91f3ca-5286-4a2e-ba04-95f0b8de2859 | 11.6911
20.19 | 28.75 | 5515.54 | 7.6 | [37.01, 53.88] | [19.94, 3.74] | [6.45, 6.45] | [10.0, 10.68] | 0 | 940.49 | 63.4 | 64.07 | -0.67 | 7.35 | 88.99 | 64 | 20.7 | 8.56 | 16.16 | 4.03 | 5.86 | 3529.94 | 1042.85 | 1176.02 | 731.31 | 5.94 | 1.56 | 4.49 | 68 | 680 | 5900 | 77.28 | 0.59 | 15.89 | 44.13 | 60 | 9 | 9 | 0.71 | 408 | 414.41 | 384278.3 | 207292.99 | 20230204-165802_0f7d7f89-c0d1-4098-b821-85ce886c8d82 | 10.1019
20.16 | 28.75 | 5503.02 | 7.6 | [37.42, 54.61] | [20.05, 3.68] | [6.65, 6.65] | [9.99, 10.82] | 0 | 940.77 | 64.12 | 64.94 | -0.82 | 7.35 | 89.01 | 64 | 20.1 | 8.58 | 15.61 | 4.55 | 5.85 | 3521.93 | 1040.71 | 1174.94 | 730.17 | 5.92 | 1.55 | 4.5 | 65.36 | 680 | 5900 | 77.48 | 0.59 | 15.98 | 43.54 | 60 | 9 | 9 | 0.72 | 408 | 414.49 | 386014.6 | 208757.88 | 20230204-165802_f7152b24-dade-4b2f-a908-ae9ed2bf1916 | 10.1174
20.19 | 28.75 | 5510.77 | 7.6 | [41.44, 58.62] | [19.95, 4.39] | [6.7, 6.7] | [10.0, 11.62] | 0 | 976.97 | 68.09 | 69.71 | -1.62 | 7.38 | 89 | 63 | 20.6 | 8.56 | 15.94 | 4.25 | 5.64 | 3526.89 | 1041.51 | 1168.23 | 729.28 | 5.86 | 1.55 | 4.51 | 66.83 | 680 | 5900 | 77.28 | 0.59 | 16.65 | 40.56 | 60 | 9 | 9 | 0.77 | 408 | 414.97 | 388436.68 | 229143.79 | 20230204-165802_cce58037-06c7-4a8f-ac9b-6477d5d91f1a | 9.0921
19.94 | 28.46 | 5528.35 | 7.6 | [39.17, 56.23] | [20.01, 4.1] | [6.54, 6.54] | [10.0, 11.15] | 0 | 958.27 | 65.72 | 66.87 | -1.15 | 7.36 | 89.01 | 62 | 20.5 | 8.52 | 15.72 | 4.22 | 5.77 | 3538.14 | 1044.99 | 1174.91 | 732.16 | 5.9 | 1.55 | 4.5 | 66.88 | 680 | 5900 | 76.9 | 0.59 | 16.12 | 42.28 | 60 | 9 | 9 | 0.74 | 408 | 414.69 | 387095.6 | 218507.23 | 20230204-165802_59065f76-cfd4-413d-a65a-cbdf29b6e001 | 9.6226
20.74 | 29.21 | 5486.54 | 7.6 | [34.96, 52.52] | [20.01, 3.43] | [6.5, 6.5] | [9.42, 10.41] | 0 | 919 | 61.47 | 62.45 | -0.98 | 7.33 | 89.07 | 83 | 18.9 | 8.47 | 16.84 | 3.9 | 5.97 | 3511.39 | 1037.88 | 1175.79 | 728.9 | 5.91 | 1.56 | 4.48 | 68.45 | 680 | 5900 | 76.47 | 0.59 | 15.39 | 45.27 | 60 | 9 | 9 | 0.69 | 408 | 414.25 | 377436.22 | 199535.99 | 20230204-165802_f7f43ea9-5675-4faa-a1dd-42022485d25e | 10.1541
20.17 | 28.71 | 5498.15 | 7.6 | [38.27, 50.18] | [19.98, 8.06] | [6.49, 6.49] | [9.98, 9.96] | 0 | 951.24 | 64.74 | 64.73 | 0.01 | 7.36 | 89.03 | 69 | 20.1 | 8.54 | 16.25 | 3.92 | 5.78 | 3518.81 | 1039.38 | 1169.88 | 728.46 | 6.5 | 1.55 | 4.5 | 68.52 | 680 | 5900 | 77.07 | 0.59 | 16.12 | 47.32 | 60 | 9 | 9 | 0.66 | 408 | 413.97 | 385658.82 | 249632.15 | 20230204-165802_e376ac16-adb0-42f1-b114-5a1e16710594 | 7.7641
20.49 | 29.05 | 5518.75 | 7.6 | [38.54, 55.67] | [19.97, 3.87] | [6.66, 6.66] | [10.0, 11.03] | 0 | 952.15 | 65.17 | 66.2 | -1.03 | 7.36 | 88.87 | 77 | 19.7 | 8.56 | 16.87 | 3.62 | 5.8 | 3532 | 1043.48 | 1175.67 | 731.66 | 5.91 | 1.56 | 4.48 | 70.27 | 680 | 5900 | 77.27 | 0.59 | 16.11 | 42.71 | 60 | 9 | 9 | 0.74 | 408 | 414.62 | 386157.51 | 214225.89 | 20230204-165802_d136b641-334d-4e33-8270-2e0107193261 | 9.8134
20.76 | 29.28 | 5501.84 | 7.61 | [40.21, 57.14] | [20.07, 4.48] | [6.34, 6.34] | [9.99, 11.33] | 0 | 968.6 | 66.62 | 67.96 | -1.34 | 7.37 | 88.99 | 76 | 19.7 | 8.51 | 16.75 | 4.02 | 5.68 | 3521.18 | 1039.49 | 1164.69 | 727.4 | 5.88 | 1.57 | 4.47 | 67.94 | 680 | 5900 | 76.85 | 0.59 | 16.42 | 41.61 | 60 | 9 | 9 | 0.76 | 408 | 414.8 | 388412.7 | 225637.44 | 20230204-165802_a9d867fd-059a-49c4-b4c6-f5974bd1e860 | 9.2908
21.13 | 29.62 | 5506.58 | 7.6 | [33.41, 55.46] | [20.05, 3.52] | [6.97, 6.97] | [5.47, 10.99] | 0 | 897.64 | 60.43 | 65.95 | -5.52 | 7.33 | 89.01 | 72 | 20.9 | 8.49 | 17.37 | 3.75 | 6.13 | 3524.21 | 1042.84 | 1190.95 | 734.55 | 5.5 | 1.58 | 4.44 | 69.37 | 680 | 5900 | 76.68 | 0.59 | 14.94 | 42.88 | 60 | 9 | 9 | 0.73 | 408 | 414.59 | 336871.19 | 209486.06 | 20230204-170424_54b7406b-43da-4c52-8fcd-f02c96498806 | 7.2708
21.31 | 29.99 | 5471.03 | 7.6 | [34.07, 54.62] | [19.9, 2.69] | [7.63, 7.63] | [7.49, 10.82] | 0 | 900.31 | 61.6 | 64.94 | -3.34 | 7.34 | 89.1 | 83 | 19.7 | 8.68 | 17.61 | 3.7 | 6.08 | 3501.46 | 1037.07 | 1189.93 | 732.01 | 5.69 | 1.57 | 4.45 | 70.13 | 680 | 5900 | 78.34 | 0.59 | 15.43 | 43.54 | 60 | 9 | 9 | 0.72 | 408 | 414.49 | 356641.54 | 197437.44 | 20230204-170424_9a50a1da-46a2-4735-a07c-50b260a7aa24 | 9.087
21.66 | 30.19 | 5459.3 | 7.6 | [31.35, 53.84] | [20.0, 3.26] | [6.92, 6.92] | [4.92, 10.67] | 0 | 876.19 | 58.27 | 64.02 | -5.75 | 7.31 | 89.18 | 79 | 20.9 | 8.53 | 18.27 | 3.39 | 6.23 | 3493.95 | 1034.39 | 1186.8 | 729.67 | 5.46 | 1.58 | 4.44 | 71.57 | 680 | 5900 | 77.03 | 0.59 | 14.73 | 44.16 | 60 | 9 | 9 | 0.71 | 408 | 414.4 | 328867.19 | 201586.88 | 20230204-170424_a11df79a-fc8a-4c36-a17b-adaccff252b7 | 7.2649
21.31 | 29.83 | 5523.8 | 7.61 | [30.72, 53.34] | [19.99, 3.09] | [6.99, 6.99] | [4.85, 10.57] | 0 | 868.38 | 57.7 | 63.42 | -5.72 | 7.3 | 88.95 | 84 | 19.8 | 8.52 | 17.83 | 3.48 | 6.36 | 3535.23 | 1046.94 | 1204.12 | 739.15 | 5.46 | 1.59 | 4.42 | 70.98 | 680 | 5900 | 76.87 | 0.59 | 14.34 | 44.58 | 60 | 9 | 9 | 0.7 | 408 | 414.34 | 327504.13 | 198147.71 | 20230204-170424_b3dfb02b-0d82-43ed-89d6-16c4e5b19db6 | 7.3834
21.57 | 30.09 | 5493.28 | 7.61 | [25.23, 48.98] | [20.5, 1.95] | [7.29, 7.29] | [4.5, 9.7] | 0 | 787.62 | 53.02 | 58.22 | -5.2 | 7.25 | 89.09 | 86 | 19.6 | 8.52 | 17.88 | 3.69 | 6.97 | 3515.7 | 1043.8 | 1227.31 | 742.37 | 5.46 | 1.6 | 4.4 | 69.77 | 680 | 5900 | 76.87 | 0.59 | 12.87 | 48.57 | 60 | 9 | 9 | 0.65 | 408 | 413.82 | 325675.96 | 171837.9 | 20230204-170424_1a46f6b8-1464-4cb7-87b0-f4933f8b8ee9 | 8.7807
21.06 | 29.55 | 5505.89 | 7.6 | [35.53, 57.45] | [19.98, 4.05] | [6.82, 6.82] | [5.39, 11.39] | 0 | 921.95 | 62.33 | 68.32 | -5.99 | 7.34 | 88.93 | 70 | 21.1 | 8.49 | 17.3 | 3.75 | 5.97 | 3523.77 | 1041.94 | 1182.55 | 732.38 | 5.47 | 1.57 | 4.46 | 69.34 | 680 | 5900 | 76.63 | 0.59 | 15.41 | 41.38 | 60 | 9 | 9 | 0.76 | 408 | 414.83 | 336881.2 | 221663.71 | 20230204-170424_45702f56-98ef-4175-821b-24c362c7ae69 | 6.5763
21.19 | 29.95 | 5467.94 | 7.6 | [30.06, 52.45] | [20.0, 1.97] | [7.92, 7.92] | [6.03, 10.39] | 0 | 851.39 | 57.98 | 62.34 | -4.36 | 7.31 | 89.04 | 83 | 19.4 | 8.76 | 17.32 | 3.86 | 6.42 | 3499.48 | 1038.32 | 1208.34 | 736.49 | 5.58 | 1.59 | 4.43 | 69.39 | 680 | 5900 | 79.09 | 0.59 | 14.59 | 45.35 | 60 | 9 | 9 | 0.69 | 408 | 414.23 | 339829.9 | 182632.22 | 20230204-170424_adf315d3-4bd4-47b8-9fb0-3bea9cab5887 | 8.9725
21.45 | 30.13 | 5476.83 | 7.6 | [38.97, 38.97] | [20.0, 20.0] | [7.81, 7.81] | [5.42, 5.42] | 0 | 944.33 | 66.78 | 66.78 | 0 | 7.37 | 88.92 | 70 | 21.9 | 8.69 | 18.05 | 3.4 | 5.8 | 3505.17 | 1037.18 | 1179.33 | 729.97 | 12.32 | 1.57 | 4.45 | 71.9 | 680 | 5900 | 78.43 | 0.59 | 16.34 | 86.92 | 60 | 9 | 9 | 0.36 | 408 | 411.25 | 341337.13 | 341337.13 | 20230204-170424_91035fab-2679-43fb-8bff-4fe8414e0a73 | 0
21.33 | 30.02 | 5491.78 | 7.6 | [29.67, 51.05] | [19.87, 1.88] | [7.75, 7.75] | [6.73, 10.11] | 0 | 850.3 | 57.29 | 60.68 | -3.39 | 7.31 | 88.98 | 85 | 19.8 | 8.68 | 17.96 | 3.37 | 6.46 | 3514.74 | 1042.69 | 1212.56 | 739.34 | 5.67 | 1.58 | 4.43 | 72.02 | 680 | 5900 | 78.4 | 0.59 | 14.36 | 46.6 | 60 | 9 | 9 | 0.67 | 408 | 414.07 | 344792.63 | 177323.27 | 20230204-170424_403ce1e5-02dc-4995-9410-f179587df1b6 | 9.5588
21.32 | 30 | 5465.16 | 7.6 | [30.89, 52.1] | [19.81, 1.93] | [7.9, 7.9] | [6.99, 10.32] | 0 | 864.14 | 58.6 | 61.93 | -3.33 | 7.32 | 89.07 | 85 | 19.5 | 8.68 | 17.66 | 3.65 | 6.32 | 3497.71 | 1037.47 | 1203.79 | 735.19 | 5.68 | 1.58 | 4.43 | 70.37 | 680 | 5900 | 78.35 | 0.59 | 14.71 | 45.66 | 60 | 9 | 9 | 0.69 | 408 | 414.19 | 347908.12 | 181124.71 | 20230204-170424_43d46bff-d2dc-423d-8a07-53fc2cd2d5cb | 9.5196
21.04 | 29.56 | 5505.97 | 7.6 | [35.98, 57.94] | [20.04, 3.98] | [6.98, 6.98] | [5.57, 11.48] | 0 | 923.87 | 63 | 68.9 | -5.9 | 7.35 | 88.97 | 67 | 21 | 8.52 | 16.82 | 4.22 | 5.96 | 3523.82 | 1042.11 | 1183.45 | 732.72 | 5.49 | 1.57 | 4.46 | 66.89 | 680 | 5900 | 76.89 | 0.59 | 15.5 | 41.04 | 60 | 9 | 9 | 0.77 | 408 | 414.89 | 340002.48 | 222351.38 | 20230204-170424_5fbf016b-9724-4156-858a-b9c47159f7f2 | 6.7152
21.33 | 30 | 5484.53 | 7.6 | [32.53, 54.45] | [19.49, 2.65] | [7.63, 7.63] | [5.7, 10.79] | 0 | 889.59 | 59.65 | 64.73 | -5.08 | 7.34 | 88.86 | 73 | 21.1 | 8.67 | 17.69 | 3.64 | 6.17 | 3510.1 | 1040.16 | 1197.91 | 735.17 | 5.53 | 1.58 | 4.44 | 70.44 | 680 | 5900 | 78.27 | 0.59 | 15.15 | 43.68 | 60 | 9 | 9 | 0.72 | 408 | 414.47 | 332225.38 | 196573.74 | 20230204-170424_fa6294b6-2f51-4461-b156-ad963cb3ab95 | 7.7427
21.32 | 29.79 | 5510.4 | 7.59 | [31.55, 53.75] | [20.07, 3.42] | [6.75, 6.75] | [5.1, 10.65] | 0 | 879.07 | 58.37 | 63.92 | -5.55 | 7.31 | 89.05 | 85 | 19.4 | 8.47 | 17.57 | 3.75 | 6.27 | 3526.65 | 1043.68 | 1194.74 | 735.56 | 5.48 | 1.58 | 4.44 | 69.3 | 680 | 5900 | 76.46 | 0.59 | 14.51 | 44.24 | 60 | 9 | 9 | 0.71 | 408 | 414.39 | 331576.44 | 203134.46 | 20230204-170424_3098fa35-14be-4597-88a1-0d6057d5753d | 7.3312
21.48 | 30.03 | 5509.01 | 7.59 | [29.45, 52.51] | [20.0, 2.73] | [7.19, 7.19] | [4.61, 10.4] | 0 | 851.17 | 56.64 | 62.43 | -5.79 | 7.3 | 88.9 | 81 | 20.1 | 8.55 | 17.75 | 3.73 | 6.47 | 3525.77 | 1044.93 | 1208.81 | 739.26 | 5.44 | 1.58 | 4.42 | 69.6 | 680 | 5900 | 77.14 | 0.59 | 14.1 | 45.29 | 60 | 9 | 9 | 0.69 | 408 | 414.24 | 324200.51 | 191510.24 | 20230204-170424_2d126446-68db-4688-afa5-5b4affe3d0bd | 7.5736
21.07 | 29.6 | 5510.87 | 7.6 | [30.25, 52.72] | [19.99, 2.69] | [7.27, 7.27] | [5.28, 10.45] | 0 | 860.13 | 57.51 | 62.68 | -5.17 | 7.3 | 88.98 | 73 | 20.5 | 8.54 | 17.13 | 3.94 | 6.41 | 3526.96 | 1045.16 | 1207.21 | 739.1 | 5.51 | 1.59 | 4.43 | 68.42 | 680 | 5900 | 77.05 | 0.59 | 14.25 | 45.11 | 60 | 9 | 9 | 0.7 | 408 | 414.27 | 331700.81 | 191670.75 | 20230204-170424_9be8e52a-556d-4e62-bb92-66462da13b61 | 7.9926
21.46 | 30.15 | 5476.65 | 7.6 | [33.12, 55.53] | [20.49, 2.62] | [7.86, 7.86] | [6.47, 11.0] | 0 | 879.71 | 61.47 | 66.01 | -4.54 | 7.33 | 89.01 | 86 | 19.7 | 8.69 | 17.98 | 3.48 | 6.23 | 3505.06 | 1038.73 | 1197.82 | 734.4 | 5.59 | 1.59 | 4.43 | 71.42 | 680 | 5900 | 78.44 | 0.59 | 15.01 | 42.83 | 60 | 9 | 9 | 0.73 | 408 | 414.6 | 352989.1 | 199441.24 | 20230204-170424_1be70015-0bd5-408c-b698-70e5caad58e7 | 8.7641

## N3
supply_temp | return_temp | ct_conductivity | ct_ph | Bore | CWRO | BoilerBD | BD | scheme | mu_conductivity | mu_flow(PV) | mu-flow(OV) | m-saving(PV-OV) | mu_ph | cooling_tower_level | relative_humidity | ambient_temp | delta_temp | wetBulb_temp | approach_temp | cond_coc | ct_tds | ct_ca | ct_alk | ct_chloride | flow_cycle | sat_index | sta_index | perf_index | system_vol | rec_rate | evap_loss | drift_loss | blowdown_coc | hold_time_index | dosing_residual | dosing_contact_time | dosing_density | dosing_continuous | dosing_initial | dosing_slug | currentOperatingCost | newOperatingCost | updatedDateTime | 445.3857
20.38 | 29.8 | 5506.5 | 7.61 | [30.31, 30.31] | [25.01, 25.01] | [10.26, 10.26] | [2.59, 2.59] | 0 | 772.06 | 65.58 | 65.58 | 0 | 7.26 | 82.03 | 44 | 22.5 | 9.41 | 14.96 | 5.42 | 7.13 | 3524.16 | 1049.01 | 1252.24 | 750.71 | 25.29 | 1.59 | 4.42 | 63.48 | 680 | 5900 | 84.98 | 0.59 | 13.86 | 181.7 | 60 | 9 | 9 | 0.17 | 408 | 409.56 | 368601.8 | 368601.8 | 20230204-160652_2002ecfe-bd5b-4d66-b73c-bc6b1d75d014 | 0
20.17 | 29.59 | 5509.1 | 7.6 | [30.5, 30.5] | [24.88, 24.88] | [10.29, 10.29] | [2.36, 2.36] | 0 | 775.57 | 65.67 | 65.67 | 0 | 7.26 | 81.97 | 46 | 21.7 | 9.42 | 14.59 | 5.58 | 7.1 | 3525.82 | 1049.49 | 1252.17 | 750.96 | 27.77 | 1.59 | 4.43 | 62.8 | 680 | 5900 | 85.04 | 0.59 | 13.93 | 199.3 | 60 | 9 | 9 | 0.16 | 408 | 409.42 | 364838.58 | 364838.58 | 20230204-160652_99555fc7-8c3b-4882-a6f7-4504d0b92880 | 0
20.91 | 30.33 | 5549.4 | 7.61 | [34.0, 34.07] | [24.93, 23.49] | [10.56, 10.56] | [8.18, 6.81] | 0 | 811.67 | 69.49 | 68.12 | 1.37 | 7.29 | 81.99 | 63 | 19.9 | 9.41 | 15.3 | 5.61 | 6.84 | 3551.62 | 1056.1 | 1248.32 | 753.4 | 10.2 | 1.61 | 4.39 | 62.67 | 680 | 5900 | 84.99 | 0.59 | 14.56 | 69.18 | 60 | 9 | 9 | 0.45 | 408 | 412.09 | 427883.33 | 396394.66 | 20230204-160652_112b7c4b-48f6-4fee-9835-c897f50db736 | 1.7973
21.18 | 30.42 | 5467 | 7.6 | [28.02, 27.11] | [25.01, 22.19] | [10.43, 10.43] | [9.16, 5.43] | 0 | 743.1 | 63.46 | 59.73 | 3.73 | 7.24 | 81.94 | 87 | 17.2 | 9.25 | 15.66 | 5.52 | 7.36 | 3498.88 | 1042.97 | 1258.53 | 749.26 | 11.69 | 1.6 | 4.4 | 62.64 | 680 | 5900 | 83.48 | 0.59 | 13.13 | 86.78 | 60 | 9 | 9 | 0.36 | 408 | 411.26 | 433461.75 | 360257.99 | 20230204-160652_e00046a6-6eb4-4c3d-a232-5e88faccf455 | 4.1783
20.94 | 30.34 | 5545.6 | 7.59 | [33.53, 33.53] | [25.01, 22.8] | [10.7, 10.7] | [8.91, 6.7] | 0 | 804.76 | 69.24 | 67.03 | 2.21 | 7.29 | 82.01 | 63 | 19.6 | 9.4 | 15.03 | 5.91 | 6.89 | 3549.18 | 1055.78 | 1251.42 | 753.94 | 10.33 | 1.59 | 4.41 | 61.4 | 680 | 5900 | 84.84 | 0.59 | 14.4 | 70.31 | 60 | 9 | 9 | 0.45 | 408 | 412.02 | 435967.34 | 386465.4 | 20230204-160652_fab0dbb8-028f-4138-acb0-0f679b3742bd | 2.8255
20.28 | 29.68 | 5502.8 | 7.59 | [33.62, 32.89] | [24.94, 22.25] | [10.61, 10.61] | [10.0, 6.57] | 0 | 807.15 | 69.17 | 65.75 | 3.42 | 7.29 | 82 | 68 | 17.8 | 9.4 | 13.99 | 6.29 | 6.82 | 3521.79 | 1047.46 | 1240.15 | 747.68 | 10.52 | 1.57 | 4.45 | 59.92 | 680 | 5900 | 84.88 | 0.59 | 14.59 | 71.69 | 60 | 9 | 9 | 0.44 | 408 | 411.94 | 446171.19 | 377724.03 | 20230204-160652_6eb5ef77-735c-4259-917e-f1e351772977 | 3.9068
20.82 | 30.21 | 5560.1 | 7.62 | [31.41, 31.76] | [24.97, 24.37] | [10.62, 10.62] | [6.61, 6.36] | 0 | 782.64 | 67 | 66.75 | 0.25 | 7.27 | 82.02 | 56 | 20.9 | 9.38 | 15.29 | 5.54 | 7.1 | 3558.46 | 1059.35 | 1263.73 | 758.13 | 10.54 | 1.62 | 4.38 | 62.89 | 680 | 5900 | 84.69 | 0.59 | 13.87 | 74.13 | 60 | 9 | 9 | 0.42 | 408 | 411.81 | 410190.43 | 400615.74 | 20230204-160652_d3ca2bbe-cc61-4fde-8bfc-9ffe281ed7a3 | 0.5465
20.78 | 30.19 | 5554.2 | 7.6 | [31.48, 31.48] | [25.07, 25.07] | [10.61, 10.61] | [4.87, 4.87] | 0 | 782.31 | 67.16 | 67.16 | 0 | 7.27 | 81.98 | 50 | 21.9 | 9.41 | 15.33 | 5.45 | 7.1 | 3554.69 | 1058.17 | 1262.03 | 757.2 | 13.79 | 1.6 | 4.4 | 63.32 | 680 | 5900 | 84.94 | 0.59 | 13.92 | 96.74 | 60 | 9 | 9 | 0.32 | 408 | 410.92 | 393848.1 | 393848.1 | 20230204-160652_270e0bcf-5337-4ce8-af48-c8601e639e04 | 0
20.08 | 29.41 | 5510.9 | 7.6 | [26.73, 26.73] | [25.08, 25.08] | [10.63, 10.63] | [2.11, 2.11] | 0 | 724.4 | 62.44 | 62.44 | 0 | 7.23 | 81.96 | 49 | 20.8 | 9.33 | 14.25 | 5.83 | 7.61 | 3526.98 | 1052.5 | 1280.16 | 758.3 | 29.58 | 1.59 | 4.42 | 61.56 | 680 | 5900 | 84.26 | 0.59 | 12.75 | 223.22 | 60 | 9 | 9 | 0.14 | 408 | 409.27 | 361777.17 | 361777.17 | 20230204-160652_39b8955b-2c79-4917-ac03-a0880fdbbd46 | 0
20.67 | 30.12 | 5538.8 | 7.61 | [28.85, 28.85] | [24.94, 24.94] | [10.64, 10.64] | [4.15, 4.15] | 0 | 752.63 | 64.43 | 64.43 | 0 | 7.25 | 81.94 | 47 | 22.2 | 9.46 | 15.16 | 5.51 | 7.36 | 3544.83 | 1056.63 | 1273.29 | 758.86 | 15.51 | 1.61 | 4.39 | 63.18 | 680 | 5900 | 85.36 | 0.59 | 13.42 | 113.42 | 60 | 9 | 9 | 0.28 | 408 | 410.49 | 382706.28 | 382706.28 | 20230204-160652_c45e770a-13ee-47de-8283-022dba0e284a | 0
20.51 | 29.92 | 5520.7 | 7.61 | [34.2, 33.24] | [25.01, 22.62] | [10.59, 10.59] | [10.0, 6.64] | 0 | 812.62 | 69.8 | 66.45 | 3.35 | 7.29 | 82 | 65 | 18.4 | 9.41 | 14.18 | 6.32 | 6.79 | 3533.25 | 1050.59 | 1241.39 | 749.38 | 10.51 | 1.6 | 4.41 | 59.8 | 680 | 5900 | 84.93 | 0.59 | 14.66 | 70.92 | 60 | 9 | 9 | 0.44 | 408 | 411.99 | 447650.99 | 383335.48 | 20230204-160652_d36adc95-942a-49a8-bced-44922c013e5e | 3.671
20.93 | 30.35 | 5551.4 | 7.63 | [33.62, 34.1] | [25.08, 23.99] | [10.1, 10.1] | [7.43, 6.82] | 0 | 809.34 | 68.8 | 68.19 | 0.61 | 7.28 | 81.95 | 62 | 20.3 | 9.42 | 15.54 | 5.39 | 6.86 | 3552.9 | 1055.84 | 1244.44 | 752.21 | 10.09 | 1.63 | 4.37 | 63.6 | 680 | 5900 | 85.06 | 0.59 | 14.52 | 69.11 | 60 | 9 | 9 | 0.45 | 408 | 412.09 | 421428.35 | 402222.89 | 20230204-160652_0e42a183-e08c-4610-b39f-fa7f74843969 | 1.0962
21.02 | 30.16 | 5490.5 | 7.6 | [26.47, 26.18] | [25.02, 21.04] | [10.45, 10.45] | [9.51, 5.24] | 0 | 722.91 | 61.94 | 57.67 | 4.27 | 7.23 | 82.14 | 84 | 18.4 | 9.14 | 16.47 | 4.55 | 7.6 | 3513.92 | 1048.41 | 1274.27 | 755.07 | 11.81 | 1.61 | 4.39 | 66.76 | 680 | 5900 | 82.51 | 0.59 | 12.51 | 89.88 | 60 | 9 | 9 | 0.35 | 408 | 411.15 | 435870.18 | 343414.01 | 20230204-160652_c3b98b40-ab60-425a-bdda-7e718e56c562 | 5.2772
20.67 | 30.08 | 5532.4 | 7.6 | [34.62, 33.36] | [24.95, 22.91] | [10.42, 10.42] | [9.97, 6.67] | 0 | 818.93 | 69.99 | 66.69 | 3.3 | 7.3 | 82 | 64 | 18.8 | 9.41 | 14.43 | 6.24 | 6.76 | 3540.74 | 1052.39 | 1240.08 | 749.89 | 10.49 | 1.59 | 4.42 | 60.11 | 680 | 5900 | 84.92 | 0.59 | 14.75 | 70.66 | 60 | 9 | 9 | 0.44 | 408 | 412 | 446713.72 | 387113.78 | 20230204-160652_5abd403a-d726-45f8-b7e4-b4cdbe6cc1a9 | 3.4018
20.72 | 30.14 | 5557.2 | 7.6 | [31.73, 31.73] | [24.91, 24.91] | [10.88, 10.88] | [5.71, 5.71] | 0 | 784.93 | 67.52 | 67.52 | 0 | 7.28 | 81.97 | 53 | 21.4 | 9.42 | 15.32 | 5.4 | 7.08 | 3556.61 | 1059.12 | 1265.07 | 758.45 | 11.83 | 1.61 | 4.39 | 63.57 | 680 | 5900 | 85.07 | 0.59 | 13.99 | 82.57 | 60 | 9 | 9 | 0.38 | 408 | 411.42 | 400809.04 | 400809.04 | 20230204-160652_4eff511c-025f-4e1b-9331-9f4deb00d65a | 0
20.39 | 29.63 | 5484.5 | 7.6 | [32.47, 32.32] | [24.96, 21.93] | [10.35, 10.35] | [9.64, 6.46] | 0 | 796.4 | 67.78 | 64.6 | 3.18 | 7.28 | 81.99 | 69 | 18.6 | 9.24 | 14.85 | 5.53 | 6.89 | 3510.08 | 1044.02 | 1237.86 | 745.46 | 10.49 | 1.58 | 4.45 | 62.56 | 680 | 5900 | 83.42 | 0.59 | 14.17 | 72.95 | 60 | 9 | 9 | 0.43 | 408 | 411.88 | 441618.2 | 371997.8 | 20230204-160652_4527b027-783a-4a3e-800c-f2dc34ec0830 | 3.9738
20.45 | 29.82 | 5520.9 | 7.6 | [28.67, 28.67] | [24.92, 24.92] | [10.64, 10.64] | [2.79, 2.79] | 0 | 750.68 | 64.23 | 64.23 | 0 | 7.25 | 82.03 | 44 | 22.6 | 9.37 | 15.05 | 5.4 | 7.35 | 3533.38 | 1053.33 | 1270.26 | 756.69 | 23.02 | 1.6 | 4.41 | 63.42 | 680 | 5900 | 84.56 | 0.59 | 13.31 | 168.91 | 60 | 9 | 9 | 0.19 | 408 | 409.67 | 368398.24 | 368398.24 | 20230204-160652_c5c6454b-51a1-4fda-aa0d-529316b48465 | 0
20.12 | 29.51 | 5507 | 7.6 | [29.97, 29.97] | [25.06, 25.06] | [10.7, 10.7] | [2.24, 2.24] | 0 | 764.28 | 65.73 | 65.73 | 0 | 7.26 | 81.92 | 48 | 21 | 9.38 | 14.28 | 5.84 | 7.21 | 3524.48 | 1050.07 | 1260.56 | 753.15 | 29.36 | 1.58 | 4.43 | 61.62 | 680 | 5900 | 84.71 | 0.59 | 13.65 | 210.51 | 60 | 9 | 9 | 0.15 | 408 | 409.34 | 365741.06 | 365741.06 | 20230204-160652_43d4023c-0c77-4e81-b9d5-c8c178f24cb5 | 0
20.1 | 29.41 | 5489.9 | 7.59 | [31.91, 31.92] | [25.1, 21.62] | [10.27, 10.27] | [9.85, 6.38] | 0 | 789.31 | 67.28 | 63.81 | 3.47 | 7.27 | 82.01 | 66 | 18.5 | 9.31 | 14.4 | 5.71 | 6.96 | 3513.54 | 1045.12 | 1240.59 | 746.46 | 10.54 | 1.57 | 4.45 | 62 | 680 | 5900 | 84.05 | 0.59 | 14.11 | 73.85 | 60 | 9 | 9 | 0.43 | 408 | 411.83 | 444837.02 | 366989.7 | 20230204-160652_74f0b3d5-caf9-4b5d-9a08-558e397f3fc9 | 4.4433
20.26 | 29.67 | 5508.3 | 7.61 | [31.12, 31.12] | [25.07, 25.07] | [9.86, 9.86] | [2.49, 2.49] | 0 | 783.68 | 66.05 | 66.05 | 0 | 7.26 | 81.99 | 45 | 22.2 | 9.41 | 14.86 | 5.4 | 7.03 | 3525.31 | 1048.24 | 1242.83 | 748.18 | 26.54 | 1.59 | 4.43 | 63.56 | 680 | 5900 | 84.97 | 0.59 | 14.09 | 189.31 | 60 | 9 | 9 | 0.17 | 408 | 409.49 | 368709.91 | 368709.91 | 20230204-160652_326510b5-793c-4963-82db-7429b7c8d3f9 | 0
20.37 | 29.75 | 5513.1 | 7.61 | [34.11, 33.26] | [25.02, 22.52] | [10.7, 10.7] | [10.0, 6.65] | 0 | 810.76 | 69.83 | 66.48 | 3.35 | 7.29 | 82.01 | 66 | 18.1 | 9.38 | 14.03 | 6.34 | 6.8 | 3528.38 | 1049.36 | 1241.55 | 748.89 | 10.5 | 1.6 | 4.42 | 59.65 | 680 | 5900 | 84.65 | 0.59 | 14.59 | 70.88 | 60 | 9 | 9 | 0.44 | 408 | 411.99 | 447728.19 | 382295.84 | 20230204-160652_93b80a35-d03b-42cf-8cf3-91bfa591a408 | 3.7347
20.48 | 29.85 | 5524.8 | 7.59 | [31.43, 31.43] | [25.1, 25.1] | [10.71, 10.71] | [3.15, 3.15] | 0 | 780.69 | 67.24 | 67.24 | 0 | 7.27 | 81.93 | 44 | 22.9 | 9.37 | 15.3 | 5.18 | 7.08 | 3535.87 | 1052.77 | 1257.04 | 753.68 | 21.38 | 1.59 | 4.42 | 64.4 | 680 | 5900 | 84.59 | 0.59 | 13.92 | 149.83 | 60 | 9 | 9 | 0.21 | 408 | 409.89 | 376690.03 | 376690.03 | 20230204-160652_a2aa0c9a-f8b5-486a-af18-6b7e3297075c | 0
20.89 | 30.16 | 5451.5 | 7.6 | [32.12, 32.8] | [24.99, 22.34] | [10.43, 10.43] | [8.53, 6.56] | 0 | 791.68 | 67.54 | 65.57 | 1.97 | 7.28 | 81.95 | 86 | 17.1 | 9.27 | 15.45 | 5.45 | 6.89 | 3488.96 | 1038.01 | 1233.04 | 741.67 | 10.3 | 1.58 | 4.43 | 62.96 | 680 | 5900 | 83.64 | 0.59 | 14.21 | 71.87 | 60 | 9 | 9 | 0.44 | 408 | 411.93 | 430421.58 | 378504.38 | 20230204-160652_f8fc4306-d166-453b-8e33-a2ee021bbac5 | 2.9633
20.81 | 30.18 | 5536.3 | 7.61 | [28.9, 28.9] | [24.98, 24.98] | [10.82, 10.82] | [3.6, 3.6] | 0 | 751.57 | 64.7 | 64.7 | 0 | 7.25 | 82.11 | 46 | 22.2 | 9.37 | 15.01 | 5.8 | 7.37 | 3543.23 | 1056.46 | 1275.08 | 759.24 | 17.96 | 1.62 | 4.38 | 61.77 | 680 | 5900 | 84.6 | 0.59 | 13.29 | 130.81 | 60 | 9 | 9 | 0.24 | 408 | 410.16 | 377744.03 | 377744.03 | 20230204-160652_7992da71-1662-43de-ae95-8d1b6fd30c32 | 0
20.09 | 29.44 | 5495 | 7.59 | [32.8, 32.36] | [25.04, 21.98] | [10.34, 10.34] | [9.97, 6.47] | 0 | 799.19 | 68.18 | 64.68 | 3.5 | 7.28 | 82.03 | 68 | 17.8 | 9.34 | 13.99 | 6.1 | 6.88 | 3516.8 | 1045.85 | 1238.6 | 746.45 | 10.54 | 1.56 | 4.46 | 60.51 | 680 | 5900 | 84.36 | 0.59 | 14.36 | 72.86 | 60 | 9 | 9 | 0.43 | 408 | 411.88 | 446236.1 | 372733.43 | 20230204-160652_a922fd44-3964-4aa1-8c28-94ef9c927970 | 4.1954
20.77 | 30.18 | 5539.2 | 7.59 | [34.49, 35.74] | [25.06, 21.41] | [10.64, 10.64] | [9.54, 7.14] | 0 | 814.71 | 70.19 | 67.79 | 2.4 | 7.29 | 81.98 | 63 | 19.3 | 9.41 | 14.76 | 6.01 | 6.8 | 3545.09 | 1054.08 | 1245.07 | 751.8 | 9.84 | 1.58 | 4.42 | 61.01 | 680 | 5900 | 84.91 | 0.59 | 14.64 | 66.04 | 60 | 9 | 9 | 0.48 | 408 | 412.28 | 443792.64 | 375725.93 | 20230204-160652_21b5fbc6-6c83-4713-9b12-4d34ca9034c0 | 3.8851
21 | 30.35 | 5418.8 | 7.59 | [27.76, 27.39] | [25.17, 25.27] | [10.51, 10.51] | [5.76, 5.49] | 0 | 737.39 | 63.44 | 63.17 | 0.27 | 7.24 | 81.98 | 86 | 16.8 | 9.35 | 15.15 | 5.84 | 7.35 | 3468.03 | 1034.05 | 1250.41 | 743.4 | 11.55 | 1.58 | 4.43 | 61.53 | 680 | 5900 | 84.39 | 0.59 | 13.29 | 85.79 | 60 | 9 | 9 | 0.37 | 408 | 411.3 | 400718.26 | 398987.06 | 20230204-161315_91352dc8-45fd-49f7-87fc-1fac06cdd8b8 | 0.098813
22.97 | 32.28 | 5509.2 | 7.6 | [28.08, 28.08] | [24.55, 24.55] | [10.41, 10.41] | [3.15, 3.15] | 0 | 749.16 | 63.04 | 63.04 | 0 | 7.25 | 81.89 | 70 | 22.6 | 9.31 | 18.7 | 4.27 | 7.35 | 3525.89 | 1051.04 | 1267.41 | 754.98 | 20.04 | 1.65 | 4.31 | 68.54 | 680 | 5900 | 84.01 | 0.59 | 13.22 | 149.77 | 60 | 9 | 9 | 0.21 | 408 | 409.89 | 366803.05 | 366803.05 | 20230204-161315_c18632b4-4ec0-4111-9546-4b496a50f4e3 | 0
21.1 | 30.37 | 5451.3 | 7.59 | [23.06, 40.44] | [24.82, 13.48] | [10.44, 10.44] | [2.0, 8.05] | 0 | 677.49 | 58.32 | 64.36 | -6.04 | 7.2 | 81.98 | 79 | 17 | 9.27 | 14.53 | 6.57 | 8.05 | 3488.83 | 1043.34 | 1291.03 | 756.2 | 7.25 | 1.61 | 4.38 | 58.53 | 680 | 5900 | 83.67 | 0.59 | 11.87 | 58.58 | 60 | 9 | 9 | 0.54 | 408 | 412.83 | 354049.14 | 291588.48 | 20230204-161315_ac5da114-592c-44bf-a45d-3aa379063127 | 3.5651
20.81 | 30.04 | 5508 | 7.59 | [22.03, 34.69] | [25.06, 17.21] | [10.36, 10.36] | [2.1, 6.92] | 0 | 659.96 | 57.45 | 62.26 | -4.81 | 7.18 | 81.96 | 81 | 17.8 | 9.23 | 15.54 | 5.28 | 8.35 | 3525.12 | 1054.78 | 1312.3 | 765.82 | 8.3 | 1.61 | 4.37 | 63.62 | 680 | 5900 | 83.28 | 0.59 | 11.34 | 68.13 | 60 | 9 | 9 | 0.46 | 408 | 412.15 | 357025.14 | 320773.29 | 20230204-161315_337ac0c4-cca7-4eb2-ae61-2531d62b51af | 2.0692
21.63 | 30.9 | 5508.1 | 7.59 | [25.43, 58.72] | [24.88, 0.68] | [10.37, 10.37] | [2.54, 11.63] | 0 | 711.05 | 60.68 | 69.77 | -9.09 | 7.22 | 81.97 | 76 | 19.9 | 9.26 | 16.94 | 4.7 | 7.75 | 3525.18 | 1052.3 | 1284.33 | 758.96 | 5.22 | 1.62 | 4.36 | 66.35 | 680 | 5900 | 83.63 | 0.59 | 12.4 | 40.52 | 60 | 9 | 9 | 0.78 | 408 | 414.98 | 362255.78 | 187036.87 | 20230204-161315_020ccc41-143d-4620-b7f7-e36c202f57e7 | 10.0011
20.96 | 30.21 | 5416.7 | 7.6 | [27.76, 27.76] | [24.77, 24.77] | [10.62, 10.62] | [2.0, 2.0] | 0 | 741.21 | 63.15 | 63.15 | 0 | 7.25 | 81.89 | 82 | 16.7 | 9.25 | 14.59 | 6.37 | 7.31 | 3466.69 | 1033.93 | 1251.32 | 743.69 | 31.63 | 1.59 | 4.41 | 59.24 | 680 | 5900 | 83.54 | 0.59 | 13.24 | 236.04 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 357637.98 | 357637.98 | 20230204-161315_c9d3decf-a54e-412b-8ef8-74b7809bf909 | 0
20.86 | 30.15 | 5439 | 7.59 | [22.91, 22.91] | [25.0, 25.0] | [10.54, 10.54] | [2.0, 2.0] | 0 | 672.72 | 58.45 | 58.45 | 0 | 7.19 | 82.07 | 78 | 16.9 | 9.29 | 14.32 | 6.54 | 8.09 | 3480.96 | 1041.29 | 1291.24 | 755.3 | 29.26 | 1.6 | 4.39 | 58.66 | 680 | 5900 | 83.82 | 0.59 | 11.83 | 235.91 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 356206.67 | 356206.67 | 20230204-161315_c0f709e6-9c3e-497a-add1-63f302d9413a | 0
22.94 | 32.19 | 5505.4 | 7.6 | [23.63, 23.63] | [25.0, 25.0] | [10.43, 10.43] | [3.02, 3.02] | 0 | 683.97 | 59.06 | 59.06 | 0 | 7.2 | 82.06 | 78 | 21.6 | 9.25 | 18.81 | 4.13 | 8.05 | 3523.46 | 1053.18 | 1298.86 | 762.38 | 19.53 | 1.66 | 4.29 | 69.12 | 680 | 5900 | 83.46 | 0.59 | 11.84 | 155.84 | 60 | 9 | 9 | 0.2 | 408 | 409.81 | 367161.05 | 367161.05 | 20230204-161315_44539f67-e12a-4365-a761-45da7ef788f4 | 0
21.34 | 30.59 | 5456.3 | 7.59 | [24.48, 58.56] | [25.13, 0.64] | [10.38, 10.38] | [2.0, 11.6] | 0 | 694.94 | 59.99 | 69.58 | -9.59 | 7.21 | 81.98 | 73 | 19.3 | 9.25 | 16 | 5.35 | 7.85 | 3492.03 | 1043.02 | 1279.62 | 753.56 | 5.17 | 1.6 | 4.38 | 63.36 | 680 | 5900 | 83.46 | 0.59 | 12.18 | 40.63 | 60 | 9 | 9 | 0.77 | 408 | 414.96 | 359052.64 | 186126.64 | 20230204-161315_abeba2c6-e346-4579-9497-9f57a5a2e960 | 9.8702
20.98 | 30.19 | 5445.2 | 7.6 | [27.31, 27.44] | [25.01, 22.63] | [10.39, 10.39] | [7.75, 5.5] | 0 | 734.38 | 62.71 | 60.46 | 2.25 | 7.23 | 82.08 | 87 | 17 | 9.21 | 15.46 | 5.51 | 7.41 | 3484.93 | 1039.14 | 1257.37 | 747.2 | 11.41 | 1.59 | 4.41 | 62.56 | 680 | 5900 | 83.17 | 0.59 | 12.96 | 85.73 | 60 | 9 | 9 | 0.37 | 408 | 411.3 | 418457.35 | 366554.27 | 20230204-161315_41eeefb3-8790-454e-93c1-b3a04ffe9dd2 | 2.9625
20.24 | 29.5 | 5484.1 | 7.6 | [21.47, 21.47] | [24.84, 24.84] | [10.46, 10.46] | [2.0, 2.0] | 0 | 653.05 | 56.77 | 56.77 | 0 | 7.18 | 82.07 | 84 | 16.5 | 9.26 | 14.63 | 5.61 | 8.4 | 3509.82 | 1050.99 | 1313.73 | 764.48 | 28.44 | 1.6 | 4.39 | 62.26 | 680 | 5900 | 83.57 | 0.59 | 11.3 | 236.07 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 352876.29 | 352876.29 | 20230204-161315_90fcb8fb-987a-45e6-86ab-f76005e7639b | 0
21.44 | 30.75 | 5465.4 | 7.6 | [24.09, 48.24] | [24.88, 8.31] | [10.47, 10.47] | [2.0, 9.57] | 0 | 691.63 | 59.44 | 67.02 | -7.58 | 7.21 | 81.99 | 86 | 16 | 9.32 | 14.37 | 7.06 | 7.9 | 3497.86 | 1045.3 | 1286.32 | 756.15 | 6.21 | 1.62 | 4.37 | 56.87 | 680 | 5900 | 84.1 | 0.59 | 12.19 | 49.22 | 60 | 9 | 9 | 0.64 | 408 | 413.74 | 355665.21 | 250607.71 | 20230204-161315_17c1cd67-cae8-437a-9652-d5c19437b078 | 5.9964
22.24 | 31.51 | 5510.5 | 7.6 | [24.97, 24.97] | [25.0, 25.0] | [10.37, 10.37] | [2.8, 2.8] | 0 | 703.37 | 60.34 | 60.34 | 0 | 7.21 | 82.05 | 74 | 21.5 | 9.27 | 18.2 | 4.05 | 7.83 | 3526.72 | 1053.05 | 1288.4 | 760.12 | 21.56 | 1.64 | 4.32 | 69.6 | 680 | 5900 | 83.64 | 0.59 | 12.24 | 168.38 | 60 | 9 | 9 | 0.19 | 408 | 409.68 | 365980.42 | 365980.42 | 20230204-161315_8eee0256-59bc-4ce3-a30a-5382b8e20255 | 0
22.57 | 31.8 | 5507.6 | 7.6 | [26.44, 26.44] | [25.0, 25.0] | [10.43, 10.43] | [2.92, 2.92] | 0 | 722.89 | 61.87 | 61.87 | 0 | 7.23 | 81.96 | 77 | 21.4 | 9.23 | 18.49 | 4.08 | 7.62 | 3524.86 | 1051.66 | 1278.12 | 757.38 | 21.15 | 1.64 | 4.32 | 69.36 | 680 | 5900 | 83.35 | 0.59 | 12.59 | 161.13 | 60 | 9 | 9 | 0.19 | 408 | 409.75 | 368580.14 | 368580.14 | 20230204-161315_5e25c133-a876-4251-b978-b5a07e0a77bd | 0
20.56 | 29.86 | 5422.6 | 7.6 | [24.97, 24.97] | [25.0, 25.0] | [10.43, 10.43] | [4.56, 4.56] | 0 | 702.96 | 60.4 | 60.4 | 0 | 7.21 | 82.08 | 86 | 16.5 | 9.3 | 14.86 | 5.7 | 7.71 | 3470.46 | 1036.38 | 1268.79 | 748.28 | 13.24 | 1.59 | 4.42 | 61.98 | 680 | 5900 | 83.91 | 0.59 | 12.5 | 103.29 | 60 | 9 | 9 | 0.3 | 408 | 410.74 | 383935.81 | 383935.81 | 20230204-161315_9307c778-4377-450c-bcb6-c822eb934dd8 | 0
22.82 | 32.15 | 5505.3 | 7.6 | [30.54, 30.54] | [25.35, 25.35] | [10.27, 10.27] | [3.25, 3.25] | 0 | 770.93 | 66.16 | 66.16 | 0 | 7.26 | 81.95 | 63 | 23.1 | 9.33 | 18.21 | 4.61 | 7.14 | 3523.39 | 1048.63 | 1250.98 | 750.19 | 20.34 | 1.64 | 4.33 | 66.95 | 680 | 5900 | 84.26 | 0.59 | 13.72 | 144.93 | 60 | 9 | 9 | 0.22 | 408 | 409.95 | 379620.12 | 379620.12 | 20230204-161315_74a80635-e644-4046-9984-5c01f8576e73 | 0
21.23 | 30.46 | 5436.4 | 7.6 | [26.88, 27.68] | [24.99, 22.88] | [10.44, 10.44] | [6.86, 5.54] | 0 | 728.73 | 62.31 | 61 | 1.31 | 7.23 | 82 | 86 | 17.3 | 9.23 | 15.64 | 5.59 | 7.46 | 3479.3 | 1037.81 | 1258.78 | 746.89 | 11.24 | 1.6 | 4.4 | 62.29 | 680 | 5900 | 83.34 | 0.59 | 12.9 | 84.99 | 60 | 9 | 9 | 0.37 | 408 | 411.33 | 408789.06 | 370277.2 | 20230204-161315_e1290cce-948e-4477-b98c-ec25375053c9 | 2.1982
20.75 | 30.04 | 5417.3 | 7.6 | [26.86, 26.86] | [25.18, 25.18] | [10.71, 10.71] | [2.0, 2.0] | 0 | 724.34 | 62.75 | 62.75 | 0 | 7.23 | 82.04 | 77 | 17 | 9.29 | 14.3 | 6.45 | 7.48 | 3467.07 | 1034.69 | 1258.94 | 745.58 | 31.3 | 1.59 | 4.42 | 59.01 | 680 | 5900 | 83.82 | 0.59 | 12.94 | 235.05 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 362131.39 | 362131.39 | 20230204-161315_20fbdb18-33e5-4e31-bfe1-76df41a7e202 | 0
20.62 | 30.02 | 5473.8 | 7.6 | [25.3, 25.3] | [25.12, 25.12] | [10.43, 10.43] | [2.0, 2.0] | 0 | 706.14 | 60.85 | 60.85 | 0 | 7.22 | 82 | 86 | 16 | 9.4 | 14.37 | 6.25 | 7.75 | 3503.23 | 1045.92 | 1278.44 | 754.72 | 30.37 | 1.6 | 4.4 | 60.05 | 680 | 5900 | 84.85 | 0.59 | 12.57 | 235.13 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 359760.64 | 359760.64 | 20230204-161315_d2524044-50c0-471e-9160-5ca0a60c9f8e | 0
22.71 | 32.03 | 5501.3 | 7.61 | [31.69, 31.69] | [24.66, 24.66] | [10.29, 10.29] | [3.29, 3.29] | 0 | 791.63 | 66.64 | 66.64 | 0 | 7.28 | 81.98 | 61 | 23 | 9.32 | 17.84 | 4.87 | 6.95 | 3520.83 | 1047.49 | 1244.3 | 748.45 | 20.23 | 1.63 | 4.34 | 65.69 | 680 | 5900 | 84.13 | 0.59 | 14.14 | 143.05 | 60 | 9 | 9 | 0.22 | 408 | 409.98 | 372714.56 | 372714.56 | 20230204-161315_6230373d-14ce-422d-8422-db746e92b142 | 0
20.53 | 29.74 | 5498.9 | 7.59 | [18.44, 27.33] | [25.04, 19.6] | [10.46, 10.46] | [2.01, 5.47] | 0 | 600.85 | 53.94 | 57.39 | -3.45 | 7.14 | 82.03 | 84 | 16.8 | 9.2 | 14.92 | 5.61 | 9.15 | 3519.3 | 1056.94 | 1351.93 | 775.09 | 9.87 | 1.62 | 4.35 | 62.11 | 680 | 5900 | 83.07 | 0.59 | 10.19 | 86.21 | 60 | 9 | 9 | 0.36 | 408 | 411.28 | 352811.67 | 329066.09 | 20230204-161315_0ef14bcd-df90-453b-922f-49d6953fa13e | 1.3553
21.9 | 31.18 | 5510.6 | 7.6 | [26.36, 35.0] | [25.25, 20.95] | [10.44, 10.44] | [2.65, 6.99] | 0 | 718.95 | 62.05 | 66.39 | -4.34 | 7.22 | 81.95 | 73 | 21.2 | 9.28 | 17.79 | 4.12 | 7.66 | 3526.78 | 1052.25 | 1279.68 | 757.92 | 8.88 | 1.63 | 4.35 | 69.27 | 680 | 5900 | 83.78 | 0.59 | 12.57 | 67.42 | 60 | 9 | 9 | 0.47 | 408 | 412.19 | 368855.65 | 367813.34 | 20230204-161315_db37e0d8-9ac0-4cc2-b48e-c9dca0847f67 | 0.059493
20.48 | 29.67 | 5437.1 | 7.6 | [23.31, 23.31] | [24.61, 24.61] | [10.47, 10.47] | [3.5, 3.5] | 0 | 683.41 | 58.39 | 58.39 | 0 | 7.2 | 82.03 | 86 | 16.4 | 9.19 | 14.76 | 5.72 | 7.96 | 3479.74 | 1040.53 | 1285.87 | 753.89 | 16.67 | 1.6 | 4.4 | 61.63 | 680 | 5900 | 82.95 | 0.59 | 11.93 | 134.56 | 60 | 9 | 9 | 0.23 | 408 | 410.1 | 366949.68 | 366949.68 | 20230204-161315_07de088f-9dd3-4dda-97cf-d19eb18679a3 | 0
20.92 | 30.04 | 5434.6 | 7.6 | [22.63, 22.63] | [25.33, 25.33] | [10.34, 10.34] | [2.61, 2.61] | 0 | 666.1 | 58.3 | 58.3 | 0 | 7.18 | 82 | 85 | 16.7 | 9.12 | 14.94 | 5.98 | 8.16 | 3478.14 | 1040.14 | 1289.28 | 754.11 | 22.33 | 1.61 | 4.38 | 60.41 | 680 | 5900 | 82.36 | 0.59 | 11.5 | 180.47 | 60 | 9 | 9 | 0.17 | 408 | 409.57 | 366097.43 | 366097.43 | 20230204-161315_47794b0e-b598-4ecd-8308-11c4a9b03d20 | 0
21.44 | 30.72 | 5462.2 | 7.6 | [23.91, 57.84] | [24.96, 0.48] | [10.4, 10.4] | [2.0, 11.45] | 0 | 688.58 | 59.27 | 68.72 | -9.45 | 7.2 | 82.01 | 79 | 17.1 | 9.27 | 14.63 | 6.81 | 7.93 | 3495.81 | 1044.64 | 1285.77 | 755.65 | 5.17 | 1.61 | 4.37 | 57.64 | 680 | 5900 | 83.72 | 0.59 | 12.08 | 41.15 | 60 | 9 | 9 | 0.76 | 408 | 414.87 | 356467.57 | 182086.31 | 20230204-161315_d9e3c717-33a5-4af7-99f2-d8211b14a626 | 9.9533
21.08 | 30.33 | 5513.9 | 7.59 | [23.42, 51.81] | [24.87, 4.47] | [10.48, 10.48] | [2.28, 10.27] | 0 | 682.06 | 58.77 | 66.76 | -7.99 | 7.2 | 81.96 | 78 | 18.9 | 9.25 | 16.23 | 4.85 | 8.08 | 3528.9 | 1055.11 | 1303.44 | 764.3 | 5.72 | 1.61 | 4.37 | 65.61 | 680 | 5900 | 83.51 | 0.59 | 11.79 | 45.88 | 60 | 9 | 9 | 0.68 | 408 | 414.16 | 357834.4 | 213749.96 | 20230204-161315_4fac19bf-be0e-4830-b177-06b8b932ab9b | 8.224
22.7 | 31.96 | 5520.2 | 7.6 | [30.26, 30.26] | [25.22, 25.22] | [10.44, 10.44] | [4.15, 4.15] | 0 | 767.78 | 65.92 | 65.92 | 0 | 7.26 | 82.03 | 63 | 22.9 | 9.26 | 18.03 | 4.67 | 7.19 | 3532.93 | 1051.94 | 1258.29 | 753.38 | 15.9 | 1.64 | 4.33 | 66.45 | 680 | 5900 | 83.55 | 0.59 | 13.5 | 113.65 | 60 | 9 | 9 | 0.28 | 408 | 410.49 | 387095.7 | 387095.7 | 20230204-161940_b5aa3c25-f98c-4548-a6bd-aefc752f69df | 0
22.46 | 31.63 | 5435.6 | 7.58 | [20.83, 59.94] | [35.0, 1.26] | [10.03, 10.03] | [6.5, 11.87] | 0 | 551.37 | 65.86 | 71.23 | -5.37 | 7.03 | 81.93 | 89 | 20.2 | 9.17 | 18.84 | 3.61 | 9.86 | 3478.78 | 1038.78 | 1306.06 | 753.63 | 5.55 | 1.62 | 4.34 | 71.73 | 680 | 5900 | 82.79 | 0.59 | 9.35 | 39.7 | 60 | 9 | 9 | 0.79 | 408 | 415.12 | 522347.2 | 197416.68 | 20230204-161940_5215ea75-d554-4ddf-8c6c-29b51d7b9639 | 18.5463
22.57 | 31.77 | 5568.8 | 7.59 | [22.67, 22.32] | [25.48, 20.87] | [10.55, 10.55] | [9.43, 4.48] | 0 | 663.89 | 58.7 | 53.74 | 4.96 | 7.18 | 82.01 | 89 | 19.9 | 9.2 | 18.55 | 4.03 | 8.39 | 3564.03 | 1066.23 | 1324.57 | 773.74 | 13.11 | 1.65 | 4.29 | 69.56 | 680 | 5900 | 83.04 | 0.59 | 11.24 | 105.22 | 60 | 9 | 9 | 0.3 | 408 | 410.69 | 437457.02 | 330285.5 | 20230204-161940_669a4f16-6e26-47c3-bd3d-f0b3d1d0b95e | 6.1171
22.87 | 32.06 | 5518.5 | 7.61 | [33.05, 34.47] | [25.0, 20.46] | [10.45, 10.45] | [10.0, 6.88] | 0 | 801.59 | 68.5 | 65.38 | 3.12 | 7.28 | 82.06 | 83 | 20.8 | 9.2 | 18.68 | 4.19 | 6.88 | 3531.84 | 1050.41 | 1244.18 | 749.8 | 9.95 | 1.64 | 4.33 | 68.7 | 680 | 5900 | 83.02 | 0.59 | 14.11 | 68.47 | 60 | 9 | 9 | 0.46 | 408 | 412.13 | 446295.46 | 360262.45 | 20230204-161940_1696e315-f61f-4157-9758-68c416da3ba7 | 4.9106
22.38 | 31.46 | 5447.8 | 7.6 | [6.1, 39.67] | [34.98, 1.33] | [10.07, 10.07] | [7.93, 7.86] | 0 | 266.59 | 51.15 | 51.07 | 0.08 | 6.81 | 82.26 | 94 | 19 | 9.08 | 18.27 | 4.11 | 20.43 | 3486.59 | 1072.68 | 1711.35 | 847.45 | 6.51 | 1.77 | 4.06 | 68.84 | 680 | 5900 | 81.97 | 0.59 | 4.22 | 59.97 | 60 | 9 | 9 | 0.52 | 408 | 412.71 | 523737.87 | 139791.5 | 20230204-161940_5ccf4030-eb78-4992-aaa0-f37b239fc28f | 21.9147
22.23 | 31.43 | 5458 | 7.57 | [16.46, 54.95] | [34.99, 0.1] | [10.23, 10.23] | [7.28, 10.88] | 0 | 480.57 | 61.68 | 65.28 | -3.6 | 6.98 | 81.79 | 94 | 19.5 | 9.2 | 18.77 | 3.46 | 11.36 | 3493.12 | 1047.97 | 1371.03 | 770.74 | 5.67 | 1.63 | 4.31 | 72.67 | 680 | 5900 | 83.05 | 0.59 | 8.02 | 43.31 | 60 | 9 | 9 | 0.73 | 408 | 414.53 | 526491.63 | 168846.85 | 20230204-161940_8298a46e-ef95-4a25-9f54-4b055c90b1fd | 20.4135
22.7 | 31.91 | 5544.1 | 7.59 | [36.36, 36.42] | [25.01, 22.22] | [10.46, 10.46] | [10.0, 7.27] | 0 | 835.44 | 71.83 | 69.1 | 2.73 | 7.31 | 81.77 | 84 | 20.7 | 9.22 | 18.71 | 3.99 | 6.64 | 3548.22 | 1054.04 | 1236.32 | 749.89 | 9.88 | 1.62 | 4.35 | 69.78 | 680 | 5900 | 83.19 | 0.59 | 14.76 | 64.79 | 60 | 9 | 9 | 0.48 | 408 | 412.36 | 449340.26 | 387422.81 | 20230204-161940_a2738943-0b03-446e-b973-af40f204db84 | 3.5341
21.75 | 31.05 | 5376 | 7.59 | [12.01, 55.97] | [35.01, 0.13] | [10.39, 10.39] | [2.0, 11.08] | 0 | 397.73 | 57.41 | 66.49 | -9.08 | 6.92 | 82.01 | 97 | 17.7 | 9.3 | 17.34 | 4.41 | 13.52 | 3440.64 | 1039.85 | 1444 | 781.02 | 5.18 | 1.66 | 4.27 | 67.83 | 680 | 5900 | 83.96 | 0.59 | 6.71 | 42.52 | 60 | 9 | 9 | 0.74 | 408 | 414.65 | 469288.05 | 172327.47 | 20230204-161940_f5f80809-4d1f-4fc5-b958-c04a0e03ef20 | 16.9498
22.8 | 31.97 | 5549.4 | 7.61 | [27.96, 27.96] | [25.09, 25.09] | [10.4, 10.4] | [5.08, 5.08] | 0 | 741.64 | 63.45 | 63.45 | 0 | 7.24 | 81.91 | 77 | 21.2 | 9.16 | 18.3 | 4.5 | 7.48 | 3551.62 | 1058.66 | 1277.55 | 760.51 | 12.5 | 1.66 | 4.3 | 67.05 | 680 | 5900 | 82.73 | 0.59 | 12.76 | 92.79 | 60 | 9 | 9 | 0.34 | 408 | 411.05 | 392944.26 | 392944.26 | 20230204-161940_71363234-a300-4312-9579-39e8b34096b7 | 0
22.75 | 32.03 | 5518.1 | 7.6 | [26.33, 36.48] | [25.05, 18.63] | [10.36, 10.36] | [3.55, 7.27] | 0 | 721.22 | 61.74 | 65.47 | -3.73 | 7.22 | 81.98 | 61 | 23 | 9.28 | 17.84 | 4.91 | 7.65 | 3531.58 | 1053.58 | 1280.27 | 758.67 | 8.49 | 1.64 | 4.31 | 65.4 | 680 | 5900 | 83.73 | 0.59 | 12.59 | 64.78 | 60 | 9 | 9 | 0.48 | 408 | 412.36 | 375444.59 | 343472.77 | 20230204-161940_55fd6eec-b5c6-42ff-94f0-3f6212519031 | 1.8249
22.71 | 31.97 | 5529.8 | 7.6 | [25.57, 25.57] | [24.7, 24.7] | [10.83, 10.83] | [4.51, 4.51] | 0 | 711.81 | 61.1 | 61.1 | 0 | 7.23 | 82.07 | 66 | 22.6 | 9.26 | 18.16 | 4.54 | 7.77 | 3539.07 | 1057.36 | 1295.85 | 764.05 | 13.56 | 1.65 | 4.3 | 67.08 | 680 | 5900 | 83.59 | 0.59 | 12.35 | 104.58 | 60 | 9 | 9 | 0.3 | 408 | 410.7 | 380576.49 | 380576.49 | 20230204-161940_7f7d2fa2-4db7-4bfc-a70a-bf94d004b1c4 | 0
22.91 | 32.18 | 5488.5 | 7.61 | [29.53, 55.62] | [25.17, 0.15] | [10.3, 10.3] | [9.94, 11.01] | 0 | 760.62 | 65 | 66.07 | -1.07 | 7.25 | 82.04 | 84 | 20.9 | 9.27 | 18.9 | 4.01 | 7.22 | 3512.64 | 1046.01 | 1253.03 | 749.44 | 5.9 | 1.64 | 4.32 | 69.78 | 680 | 5900 | 83.64 | 0.59 | 13.46 | 42.79 | 60 | 9 | 9 | 0.73 | 408 | 414.61 | 444692.95 | 171541.36 | 20230204-161940_6bb85cae-d577-4efa-9e80-71e64d32fdac | 15.5908
22.61 | 31.85 | 5407.2 | 7.6 | [15.38, 55.72] | [35.0, 0.4] | [10.08, 10.08] | [5.29, 11.03] | 0 | 462.03 | 60.46 | 66.2 | -5.74 | 6.96 | 82.1 | 91 | 19.6 | 9.24 | 18.5 | 4.11 | 11.7 | 3460.61 | 1039.12 | 1372.21 | 766.46 | 5.48 | 1.67 | 4.27 | 69.21 | 680 | 5900 | 83.41 | 0.59 | 7.79 | 42.71 | 60 | 9 | 9 | 0.74 | 408 | 414.62 | 505241.09 | 174721.72 | 20230204-161940_330582db-8de1-4789-af78-f5c23e0515fd | 18.8653
22.73 | 32.01 | 5506.9 | 7.61 | [25.98, 48.86] | [25.24, 8.72] | [10.31, 10.31] | [3.35, 9.7] | 0 | 714.91 | 61.53 | 67.89 | -6.36 | 7.22 | 82.12 | 62 | 23.3 | 9.28 | 18.25 | 4.48 | 7.7 | 3524.42 | 1051.52 | 1279.35 | 757.43 | 6.35 | 1.65 | 4.31 | 67.47 | 680 | 5900 | 83.79 | 0.59 | 12.5 | 48.59 | 60 | 9 | 9 | 0.65 | 408 | 413.82 | 375346.5 | 257281.17 | 20230204-161940_4e8d8934-b950-42ab-91de-02eab0731f3f | 6.7389
22.8 | 31.88 | 5583.3 | 7.59 | [27.18, 55.53] | [25.0, 0.05] | [10.39, 10.39] | [7.6, 11.0] | 0 | 732.63 | 62.57 | 65.97 | -3.4 | 7.23 | 81.86 | 84 | 20.5 | 9.08 | 18.51 | 4.29 | 7.62 | 3573.31 | 1065.59 | 1290.2 | 766.39 | 5.69 | 1.65 | 4.3 | 67.92 | 680 | 5900 | 81.98 | 0.59 | 12.38 | 42.86 | 60 | 9 | 9 | 0.73 | 408 | 414.6 | 416779.6 | 170050.59 | 20230204-161940_49b0d643-eca4-4310-95e9-df8668edea2c | 14.0827
22.68 | 31.68 | 5595.7 | 7.6 | [21.56, 46.58] | [24.89, 2.91] | [10.51, 10.51] | [6.21, 9.23] | 0 | 653.55 | 56.96 | 60 | -3.04 | 7.18 | 81.85 | 89 | 19.4 | 9 | 18.06 | 4.63 | 8.56 | 3581.25 | 1072.42 | 1340.69 | 780.13 | 6.17 | 1.67 | 4.26 | 66.05 | 680 | 5900 | 81.25 | 0.59 | 10.74 | 51.05 | 60 | 9 | 9 | 0.62 | 408 | 413.54 | 396466.1 | 179449.06 | 20230204-161940_b8b608f7-a603-484a-8c2a-a4d159c353b0 | 12.3868
22.39 | 31.69 | 5390.2 | 7.58 | [13.03, 15.89] | [35.04, 33.42] | [10.61, 10.61] | [2.0, 3.24] | 0 | 417 | 58.68 | 59.92 | -1.24 | 6.94 | 82.03 | 92 | 19.1 | 9.3 | 18.13 | 4.26 | 12.93 | 3449.73 | 1041.35 | 1428.52 | 779.09 | 18.12 | 1.66 | 4.26 | 68.59 | 680 | 5900 | 83.97 | 0.59 | 7.04 | 145.49 | 60 | 9 | 9 | 0.22 | 408 | 409.94 | 470766.43 | 466013.05 | 20230204-161940_b098edc8-b0f1-4c75-a2af-7f67c5b1a006 | 0.27131
21.57 | 30.91 | 5374.2 | 7.6 | [12.77, 55.53] | [34.06, 0.3] | [10.15, 10.15] | [2.0, 11.0] | 0 | 419.56 | 56.98 | 65.98 | -9 | 6.94 | 81.98 | 97 | 17.3 | 9.34 | 16.94 | 4.63 | 12.81 | 3439.49 | 1037.44 | 1417.03 | 774.72 | 5.18 | 1.66 | 4.28 | 66.86 | 680 | 5900 | 84.31 | 0.59 | 7.14 | 42.85 | 60 | 9 | 9 | 0.73 | 408 | 414.6 | 458097.63 | 172948.87 | 20230204-161940_78126632-cfb1-4c76-bca9-725a05622f37 | 16.2756
22.86 | 32.11 | 5469 | 7.61 | [23.25, 54.01] | [34.88, 5.21] | [10.39, 10.39] | [9.63, 10.71] | 0 | 585.88 | 68.52 | 69.61 | -1.09 | 7.07 | 82.2 | 83 | 20.6 | 9.25 | 18.48 | 4.38 | 9.33 | 3500.16 | 1044.26 | 1297.98 | 755.13 | 6.4 | 1.66 | 4.29 | 67.88 | 680 | 5900 | 83.5 | 0.59 | 10.02 | 44 | 60 | 9 | 9 | 0.71 | 408 | 414.43 | 555114.38 | 229090.64 | 20230204-161940_d0654960-d4a8-4ebf-89e8-4ef79766dafd | 18.6087
22.3 | 31.62 | 5380 | 7.59 | [12.5, 19.75] | [35.0, 29.75] | [10.4, 10.4] | [2.0, 3.99] | 0 | 407.58 | 57.9 | 59.9 | -2 | 6.93 | 82 | 95 | 18.6 | 9.32 | 17.99 | 4.3 | 13.2 | 3443.2 | 1039.65 | 1432.69 | 778.78 | 14.5 | 1.67 | 4.25 | 68.42 | 680 | 5900 | 84.13 | 0.59 | 6.9 | 118.01 | 60 | 9 | 9 | 0.27 | 408 | 410.4 | 469616.14 | 431814.64 | 20230204-161940_24999d64-ae9a-4bf1-9e01-545f40a200af | 2.1576
22.43 | 31.77 | 5392.5 | 7.6 | [13.83, 57.19] | [34.96, 0.59] | [10.17, 10.17] | [2.33, 11.33] | 0 | 433.68 | 58.96 | 67.95 | -8.99 | 6.95 | 82.01 | 90 | 19.4 | 9.33 | 18.18 | 4.25 | 12.43 | 3451.2 | 1038.91 | 1400.01 | 771.82 | 5.21 | 1.67 | 4.26 | 68.69 | 680 | 5900 | 84.25 | 0.59 | 7.37 | 41.61 | 60 | 9 | 9 | 0.76 | 408 | 414.8 | 473394.51 | 181312.39 | 20230204-161940_55dd3712-5842-40af-bdac-f0237564dada | 16.6714
21.99 | 31.32 | 5373.9 | 7.59 | [12.8, 56.75] | [35.0, 0.28] | [10.39, 10.39] | [2.0, 11.24] | 0 | 413.32 | 58.19 | 67.42 | -9.23 | 6.93 | 82.01 | 96 | 18.1 | 9.32 | 17.62 | 4.38 | 13 | 3439.3 | 1037.88 | 1423.75 | 776.18 | 5.18 | 1.66 | 4.27 | 68.05 | 680 | 5900 | 84.16 | 0.59 | 7.01 | 41.93 | 60 | 9 | 9 | 0.75 | 408 | 414.74 | 469871.01 | 176430.94 | 20230204-161940_7f6e81ff-6745-494e-aae9-8fb1819f0153 | 16.7489
22.79 | 31.97 | 5434.7 | 7.6 | [18.57, 55.29] | [35.01, 0.39] | [10.01, 10.01] | [8.85, 10.95] | 0 | 516.3 | 63.59 | 65.69 | -2.1 | 7.01 | 82.05 | 88 | 20.1 | 9.18 | 18.62 | 4.17 | 10.53 | 3478.21 | 1040.55 | 1330.93 | 759.21 | 5.81 | 1.66 | 4.28 | 68.74 | 680 | 5900 | 82.85 | 0.59 | 8.7 | 43.04 | 60 | 9 | 9 | 0.73 | 408 | 414.57 | 544288.39 | 173236.65 | 20230204-161940_b6524f31-8bbc-4434-a8eb-a220a1e50913 | 21.1788
22.52 | 31.84 | 5396.9 | 7.6 | [15.34, 57.08] | [34.99, 0.73] | [10.01, 10.01] | [3.83, 11.3] | 0 | 461.46 | 60.34 | 67.82 | -7.48 | 6.96 | 82.02 | 90 | 19.6 | 9.32 | 18.38 | 4.14 | 11.7 | 3454.02 | 1037 | 1368.81 | 764.7 | 5.34 | 1.66 | 4.27 | 69.23 | 680 | 5900 | 84.15 | 0.59 | 7.87 | 41.69 | 60 | 9 | 9 | 0.75 | 408 | 414.78 | 490240.79 | 182581.22 | 20230204-161940_f791e109-5949-460c-9ee6-75d59a50a7f3 | 17.5605
22.72 | 31.98 | 5520.2 | 7.6 | [30.71, 30.71] | [24.74, 24.74] | [10.34, 10.34] | [3.84, 3.84] | 0 | 779.17 | 65.79 | 65.79 | 0 | 7.27 | 81.92 | 62 | 22.9 | 9.27 | 17.89 | 4.82 | 7.08 | 3532.93 | 1051.62 | 1254.28 | 752.46 | 17.11 | 1.63 | 4.34 | 65.77 | 680 | 5900 | 83.64 | 0.59 | 13.75 | 122.56 | 60 | 9 | 9 | 0.26 | 408 | 410.31 | 378382.86 | 378382.86 | 20230204-161940_16b7d7f2-6364-44cd-b718-af28e797449f | 0
22.8 | 31.9 | 5548.1 | 7.6 | [28.52, 27.68] | [25.0, 22.88] | [10.43, 10.43] | [8.51, 5.54] | 0 | 749.34 | 63.95 | 60.99 | 2.96 | 7.25 | 82.05 | 90 | 19.8 | 9.09 | 18.57 | 4.23 | 7.4 | 3550.78 | 1058.18 | 1274.28 | 759.65 | 11.53 | 1.64 | 4.31 | 68.26 | 680 | 5900 | 82.09 | 0.59 | 12.82 | 84.99 | 60 | 9 | 9 | 0.37 | 408 | 411.33 | 427196.34 | 370315.89 | 20230204-161940_011fb6e1-ac91-412d-8071-8965b7627169 | 3.2466
21.4 | 30.67 | 5387.4 | 7.61 | [15.96, 49.86] | [30.03, 4.01] | [10.38, 10.38] | [2.0, 9.88] | 0 | 509.83 | 56.37 | 64.25 | -7.88 | 7.04 | 81.91 | 97 | 16.9 | 9.27 | 16.54 | 4.87 | 10.57 | 3447.94 | 1036.98 | 1361.45 | 765.63 | 5.7 | 1.65 | 4.31 | 65.58 | 680 | 5900 | 83.69 | 0.59 | 8.75 | 47.68 | 60 | 9 | 9 | 0.66 | 408 | 413.93 | 411733.23 | 202356.55 | 20230204-162602_6cb08677-e976-45ae-87db-f4548b79c838 | 11.9507
22.87 | 32.16 | 5409.1 | 7.6 | [16.28, 16.28] | [29.73, 29.73] | [10.84, 10.84] | [2.0, 2.0] | 0 | 516.56 | 56.85 | 56.85 | 0 | 7.05 | 82.03 | 86 | 21 | 9.29 | 19.25 | 3.62 | 10.47 | 3461.82 | 1042.19 | 1372.14 | 770.86 | 28.47 | 1.67 | 4.25 | 71.96 | 680 | 5900 | 83.84 | 0.59 | 8.85 | 236.03 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 408591.43 | 408591.43 | 20230204-162602_f75dbaf7-3d38-45a0-93cd-f27506314615 | 0
23.03 | 32.34 | 5389.6 | 7.6 | [19.15, 28.63] | [29.82, 24.08] | [10.39, 10.39] | [2.0, 5.74] | 0 | 566.97 | 59.36 | 63.1 | -3.74 | 7.08 | 82.01 | 84 | 21.3 | 9.32 | 19.29 | 3.74 | 9.51 | 3449.34 | 1033.69 | 1317.54 | 755.41 | 10.35 | 1.65 | 4.29 | 71.35 | 680 | 5900 | 84.09 | 0.59 | 9.89 | 82.16 | 60 | 9 | 9 | 0.38 | 408 | 411.44 | 411900.71 | 387730.77 | 20230204-162602_db6e0a5f-c355-4cd8-8129-4f8633a2f92e | 1.3796
21.06 | 30.32 | 5390.2 | 7.61 | [14.98, 49.2] | [30.2, 3.73] | [10.46, 10.46] | [2.0, 9.75] | 0 | 489.95 | 55.64 | 63.39 | -7.75 | 7.02 | 82.04 | 98 | 16.7 | 9.26 | 16.45 | 4.61 | 11 | 3449.73 | 1039.17 | 1381.17 | 770.62 | 5.71 | 1.65 | 4.31 | 66.78 | 680 | 5900 | 83.59 | 0.59 | 8.36 | 48.32 | 60 | 9 | 9 | 0.65 | 408 | 413.85 | 413004.32 | 197108.48 | 20230204-162602_a0537208-1951-4fe6-b9d7-d3f77f3698b1 | 12.3228
21.62 | 30.91 | 5391 | 7.6 | [14.63, 14.63] | [30.0, 30.0] | [10.71, 10.71] | [2.0, 2.0] | 0 | 484.25 | 55.34 | 55.34 | 0 | 7.03 | 82.01 | 98 | 17.1 | 9.28 | 16.85 | 4.77 | 11.13 | 3450.24 | 1040.74 | 1393.75 | 774.25 | 27.66 | 1.66 | 4.29 | 66.05 | 680 | 5900 | 83.8 | 0.59 | 8.27 | 235.61 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 410378.54 | 410378.54 | 20230204-162602_1ad30b17-4fbc-4f3e-a995-e7e0ad0ce9a1 | 0
21.29 | 30.56 | 5404.4 | 7.6 | [16.08, 23.71] | [30.29, 25.42] | [10.44, 10.44] | [2.0, 4.77] | 0 | 509.64 | 56.81 | 59.57 | -2.76 | 7.04 | 82.03 | 97 | 16.8 | 9.27 | 16.44 | 4.85 | 10.6 | 3458.82 | 1040.2 | 1365.39 | 767.92 | 11.92 | 1.64 | 4.32 | 65.64 | 680 | 5900 | 83.7 | 0.59 | 8.71 | 98.88 | 60 | 9 | 9 | 0.32 | 408 | 410.86 | 414954.92 | 390144.58 | 20230204-162602_35725284-e655-4bdd-9c7f-64255cac374b | 1.4161
23.08 | 32.43 | 5390.1 | 7.6 | [18.67, 35.79] | [30.05, 18.07] | [10.37, 10.37] | [2.0, 7.14] | 0 | 557.05 | 59.09 | 64.23 | -5.14 | 7.07 | 82.03 | 85 | 21 | 9.35 | 19.12 | 3.96 | 9.68 | 3449.66 | 1034.19 | 1323.32 | 756.7 | 8.28 | 1.65 | 4.29 | 70.25 | 680 | 5900 | 84.39 | 0.59 | 9.73 | 66.03 | 60 | 9 | 9 | 0.48 | 408 | 412.28 | 414282.41 | 334565.9 | 20230204-162602_6402f738-41ad-49a3-925b-08f6a2748f4a | 4.55
21.26 | 30.57 | 5386.5 | 7.59 | [16.16, 16.16] | [30.25, 30.25] | [10.53, 10.53] | [2.0, 2.0] | 0 | 511.08 | 56.94 | 56.94 | 0 | 7.04 | 82.01 | 98 | 16.8 | 9.3 | 16.55 | 4.71 | 10.54 | 3447.36 | 1036.91 | 1361.54 | 765.69 | 28.48 | 1.62 | 4.34 | 66.39 | 680 | 5900 | 83.99 | 0.59 | 8.8 | 235.73 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 414701.42 | 414701.42 | 20230204-162602_8f298c37-cf64-402d-94f8-78d928747063 | 0
21.23 | 30.49 | 5400.7 | 7.59 | [16.91, 16.91] | [29.68, 29.68] | [10.29, 10.29] | [2.0, 2.0] | 0 | 530.42 | 56.88 | 56.88 | 0 | 7.05 | 81.99 | 97 | 16.9 | 9.27 | 16.54 | 4.69 | 10.18 | 3456.45 | 1038.11 | 1347.67 | 763.46 | 28.37 | 1.62 | 4.35 | 66.37 | 680 | 5900 | 83.64 | 0.59 | 9.11 | 235.06 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 408231.36 | 408231.36 | 20230204-162602_6ee43f9d-1c3f-490d-a050-08ec37dfcaeb | 0
22.75 | 32.08 | 5393.7 | 7.6 | [21.15, 21.15] | [30.28, 30.28] | [10.39, 10.39] | [2.0, 2.0] | 0 | 594.48 | 61.82 | 61.82 | 0 | 7.1 | 81.97 | 85 | 21 | 9.32 | 19.12 | 3.63 | 9.07 | 3451.97 | 1032.52 | 1297.08 | 750.64 | 30.94 | 1.64 | 4.32 | 71.98 | 680 | 5900 | 84.16 | 0.59 | 10.42 | 235.85 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 419262.63 | 419262.63 | 20230204-162602_90ef631e-a868-43ff-9ee3-a9d271025600 | 0
23.1 | 32.45 | 5400.8 | 7.6 | [19.02, 19.02] | [29.99, 29.99] | [11.2, 11.2] | [2.0, 2.0] | 0 | 559.65 | 60.21 | 60.21 | 0 | 7.09 | 82.02 | 80 | 22 | 9.34 | 19.45 | 3.65 | 9.65 | 3456.51 | 1038.06 | 1338.45 | 762.37 | 30.12 | 1.66 | 4.27 | 71.88 | 680 | 5900 | 84.35 | 0.59 | 9.75 | 235.74 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 414585.24 | 414585.24 | 20230204-162602_99045306-03a0-4762-9b7c-0c8277dbc925 | 0
22.3 | 31.64 | 5397.5 | 7.6 | [17.53, 17.53] | [30.3, 30.3] | [10.31, 10.31] | [2.0, 2.0] | 0 | 535.73 | 58.14 | 58.14 | 0 | 7.05 | 81.95 | 90 | 19.7 | 9.34 | 18.47 | 3.83 | 10.07 | 3454.4 | 1036.65 | 1339.02 | 760.84 | 29.07 | 1.65 | 4.3 | 70.93 | 680 | 5900 | 84.33 | 0.59 | 9.29 | 235.64 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 416265.88 | 416265.88 | 20230204-162602_f6a6d0fb-a0f1-4555-93d1-4688dd52685a | 0
22.51 | 31.86 | 5394.4 | 7.6 | [18.61, 18.61] | [29.7, 29.7] | [10.35, 10.35] | [2.0, 2.0] | 0 | 559.15 | 58.66 | 58.66 | 0 | 7.08 | 81.98 | 85 | 20.5 | 9.35 | 18.64 | 3.87 | 9.65 | 3452.42 | 1035.12 | 1324.6 | 757.5 | 29.3 | 1.65 | 4.3 | 70.71 | 680 | 5900 | 84.42 | 0.59 | 9.76 | 235.37 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 409931.53 | 409931.53 | 20230204-162602_55c4c123-e1f6-47b3-9608-d1900a8c47f8 | 0
21.34 | 30.61 | 5402.5 | 7.59 | [17.29, 50.99] | [29.83, 4.23] | [10.48, 10.48] | [2.01, 10.11] | 0 | 535.03 | 57.6 | 65.7 | -8.1 | 7.06 | 81.93 | 96 | 17.1 | 9.28 | 16.62 | 4.72 | 10.1 | 3457.6 | 1038.5 | 1347 | 763.66 | 5.7 | 1.63 | 4.34 | 66.28 | 680 | 5900 | 83.74 | 0.59 | 9.21 | 46.62 | 60 | 9 | 9 | 0.67 | 408 | 414.06 | 410491.18 | 208449.73 | 20230204-162602_8be5066a-76cd-4808-9a0c-89cdb3de2d8a | 11.532
23.05 | 32.34 | 5405.2 | 7.6 | [16.93, 16.93] | [29.76, 29.76] | [10.8, 10.8] | [2.0, 2.0] | 0 | 527.89 | 57.49 | 57.49 | 0 | 7.06 | 82.01 | 79 | 22 | 9.29 | 19.32 | 3.73 | 10.24 | 3459.33 | 1040.43 | 1360.16 | 767.57 | 28.7 | 1.67 | 4.26 | 71.33 | 680 | 5900 | 83.84 | 0.59 | 9.07 | 235.25 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 409672.96 | 409672.96 | 20230204-162602_68e631f7-fe63-4606-be36-47dc9a792f90 | 0
22.84 | 32.15 | 5403.8 | 7.61 | [18.82, 25.08] | [30.11, 26.89] | [11.04, 11.04] | [2.0, 5.04] | 0 | 556.09 | 59.97 | 63.01 | -3.04 | 7.08 | 82 | 89 | 20.4 | 9.32 | 19.04 | 3.8 | 9.72 | 3458.43 | 1038.42 | 1338.61 | 762.39 | 11.9 | 1.67 | 4.27 | 71.05 | 680 | 5900 | 84.1 | 0.59 | 9.65 | 93.47 | 60 | 9 | 9 | 0.34 | 408 | 411.02 | 415827.08 | 412695.93 | 20230204-162602_432aac77-3e85-4667-84ed-4536c19bc1a3 | 0.17872
21.33 | 30.51 | 5403.6 | 7.61 | [13.79, 47.87] | [30.0, 3.41] | [10.4, 10.4] | [2.0, 9.49] | 0 | 468.96 | 54.19 | 61.68 | -7.49 | 7.01 | 82.01 | 97 | 17.1 | 9.18 | 16.74 | 4.6 | 11.52 | 3458.3 | 1043.6 | 1406.09 | 777.7 | 5.71 | 1.66 | 4.29 | 66.62 | 680 | 5900 | 82.84 | 0.59 | 7.87 | 49.66 | 60 | 9 | 9 | 0.63 | 408 | 413.69 | 409350.51 | 189228.28 | 20230204-162602_df9e1869-b550-4c2b-8981-f7679fbcbf21 | 12.5641
22.09 | 31.36 | 5403.1 | 7.6 | [15.16, 15.16] | [29.69, 29.69] | [10.48, 10.48] | [1.99, 1.99] | 0 | 497.55 | 55.33 | 55.33 | 0 | 7.03 | 82.03 | 95 | 18.7 | 9.27 | 18.09 | 4 | 10.86 | 3457.98 | 1041.62 | 1381.44 | 772.09 | 27.75 | 1.66 | 4.28 | 69.88 | 680 | 5900 | 83.68 | 0.59 | 8.49 | 236.33 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 406821.37 | 406821.37 | 20230204-162602_ebe99646-f5e2-422b-98da-f07c1bd2b4c9 | 0
21.83 | 31.04 | 5417.5 | 7.61 | [15.09, 15.09] | [30.16, 30.16] | [10.47, 10.47] | [2.0, 2.0] | 0 | 492.38 | 55.72 | 55.72 | 0 | 7.03 | 81.95 | 97 | 18.1 | 9.21 | 17.74 | 4.09 | 11 | 3467.2 | 1044.31 | 1386.35 | 774.14 | 27.8 | 1.66 | 4.28 | 69.26 | 680 | 5900 | 83.18 | 0.59 | 8.32 | 235.16 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 412601.99 | 412601.99 | 20230204-162602_f7f0ce25-407c-4b30-968e-a967772b3d1d | 0
21.12 | 30.4 | 5387 | 7.6 | [16.37, 16.37] | [29.76, 29.76] | [10.21, 10.21] | [2.0, 2.0] | 0 | 520.41 | 56.34 | 56.34 | 0 | 7.04 | 82 | 98 | 16.6 | 9.28 | 16.35 | 4.77 | 10.35 | 3447.68 | 1035.92 | 1350.65 | 762.89 | 28.14 | 1.63 | 4.34 | 66.03 | 680 | 5900 | 83.75 | 0.59 | 8.96 | 235.4 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 408586.77 | 408586.77 | 20230204-162602_59b604ee-f80e-429e-9f33-a8d2fe874ab9 | 0
23.18 | 32.49 | 5401 | 7.6 | [21.42, 21.42] | [29.99, 29.99] | [10.87, 10.87] | [2.0, 2.0] | 0 | 598.77 | 62.28 | 62.28 | 0 | 7.11 | 81.95 | 80 | 22 | 9.32 | 19.45 | 3.73 | 9.02 | 3456.64 | 1034.89 | 1304.85 | 753.81 | 31.14 | 1.66 | 4.29 | 71.43 | 680 | 5900 | 84.1 | 0.59 | 10.49 | 235.64 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 416455.69 | 416455.69 | 20230204-162602_80f6217c-e0f0-4c1a-b291-b25f8547d817 | 0
21.42 | 30.74 | 5386.9 | 7.6 | [17.06, 17.06] | [30.0, 30.0] | [10.6, 10.6] | [2.0, 2.0] | 0 | 529.06 | 57.66 | 57.66 | 0 | 7.06 | 81.97 | 98 | 17.1 | 9.32 | 16.85 | 4.56 | 10.18 | 3447.62 | 1036.08 | 1349.12 | 762.99 | 28.85 | 1.63 | 4.33 | 67.13 | 680 | 5900 | 84.13 | 0.59 | 9.16 | 235.81 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 412479.67 | 412479.67 | 20230204-162602_b4176341-9e94-4677-8a3b-64dc122428ec | 0
21.42 | 30.62 | 5411.2 | 7.6 | [13.5, 13.5] | [30.14, 30.14] | [10.4, 10.4] | [2.0, 2.0] | 0 | 461.83 | 54.04 | 54.04 | 0 | 7 | 82.05 | 97 | 17.3 | 9.2 | 16.94 | 4.49 | 11.72 | 3463.17 | 1045.59 | 1414.75 | 780.32 | 27.05 | 1.66 | 4.28 | 67.21 | 680 | 5900 | 83.02 | 0.59 | 7.75 | 235.87 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 410927.93 | 410927.93 | 20230204-162602_99be4bf4-0735-420d-b4ff-792e3783208c | 0
23.11 | 32.39 | 5407.5 | 7.6 | [19.9, 19.9] | [29.98, 29.98] | [10.96, 10.96] | [2.0, 2.0] | 0 | 574.94 | 60.84 | 60.84 | 0 | 7.1 | 81.99 | 78 | 22 | 9.28 | 19.19 | 3.92 | 9.41 | 3460.8 | 1037.81 | 1324.75 | 759.29 | 30.36 | 1.66 | 4.28 | 70.32 | 680 | 5900 | 83.81 | 0.59 | 9.97 | 235.16 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 415044.93 | 415044.93 | 20230204-162602_1682a359-b710-4c8c-b165-638bbb24d498 | 0
21.38 | 30.59 | 5394.2 | 7.6 | [16.71, 36.95] | [30.0, 15.12] | [10.48, 10.48] | [2.0, 7.36] | 0 | 523.2 | 57.19 | 62.55 | -5.36 | 7.05 | 82.02 | 98 | 17 | 9.21 | 16.75 | 4.62 | 10.31 | 3452.29 | 1037.61 | 1353.74 | 764.52 | 7.77 | 1.64 | 4.32 | 66.59 | 680 | 5900 | 83.16 | 0.59 | 8.93 | 64.04 | 60 | 9 | 9 | 0.49 | 408 | 412.41 | 412063.39 | 301692.33 | 20230204-162602_8e4c90e8-c938-4dbc-85f2-1b8b57d6a6ed | 6.2997
22.94 | 32.22 | 5406.3 | 7.59 | [19.42, 19.42] | [30.21, 30.21] | [11.58, 11.58] | [2.0, 2.0] | 0 | 562.6 | 61.21 | 61.21 | 0 | 7.1 | 81.98 | 85 | 20.8 | 9.28 | 18.93 | 4.01 | 9.61 | 3460.03 | 1039.59 | 1342.44 | 764.16 | 30.65 | 1.65 | 4.28 | 69.81 | 680 | 5900 | 83.78 | 0.59 | 9.73 | 235.93 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 418005.7 | 418005.7 | 20230204-162602_4e869081-fd05-470c-99e3-3f4cf39634b1 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.51 | 31.65 | 5458.8 | 7.6 | [19.31, 19.31] | [29.99, 29.99] | [8.36, 8.36] | [2.0, 2.0] | 0 | 577.42 | 57.66 | 57.66 | 0 | 7.05 | 81.94 | 85 | 20.4 | 9.13 | 18.54 | 3.97 | 9.45 | 3493.63 | 1041.31 | 1290.52 | 751.64 | 28.76 | 1.64 | 4.32 | 69.68 | 680 | 5900 | 82.45 | 0.59 | 9.75 | 235.04 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 412425.5 | 412425.5 | 20230204-163228_d4aac477-4f9f-441e-9337-757c6a96df4a | 0
22.79 | 32.04 | 5429.7 | 7.61 | [21.86, 21.86] | [29.98, 29.98] | [9.64, 9.64] | [2.0, 2.0] | 0 | 611.68 | 61.48 | 61.48 | 0 | 7.1 | 81.99 | 76 | 21.8 | 9.25 | 18.74 | 4.05 | 8.88 | 3475.01 | 1037.08 | 1284.6 | 749.77 | 30.82 | 1.65 | 4.31 | 69.54 | 680 | 5900 | 83.52 | 0.59 | 10.6 | 236.2 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 415579.25 | 415579.25 | 20230204-163228_f4d9136d-7c5f-4115-bed5-81e02ade9b44 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23.02 | 32.36 | 5407 | 7.61 | [19.82, 19.82] | [29.99, 29.99] | [10.85, 10.85] | [2.0, 2.0] | 0 | 574.18 | 60.66 | 60.66 | 0 | 7.09 | 81.99 | 77 | 22.2 | 9.35 | 19.25 | 3.76 | 9.42 | 3460.48 | 1037.51 | 1323.34 | 758.76 | 30.37 | 1.67 | 4.28 | 71.29 | 680 | 5900 | 84.39 | 0.59 | 10.03 | 235.92 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 414927.2 | 414927.2 | 20230204-163228_e4972e1b-d56c-4881-86fe-46218ff5ef74 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.23 | 31.1 | 5482.3 | 7.61 | [21.36, 34.67] | [30.02, 21.63] | [6.02, 6.02] | [2.0, 6.92] | 0 | 622.94 | 57.4 | 62.32 | -4.92 | 7.04 | 82.02 | 87 | 19.7 | 8.86 | 18.1 | 4.13 | 8.8 | 3508.67 | 1038.31 | 1230.3 | 736.21 | 8.29 | 1.62 | 4.37 | 68.22 | 680 | 5900 | 80.02 | 0.59 | 10.26 | 68.05 | 60 | 9 | 9 | 0.46 | 408 | 412.15 | 412462.13 | 371334.94 | 20230204-163228_05325a78-0675-4039-8882-cffcc3b78bc6 | 2.3474
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.88 | 32.2 | 5411.7 | 7.61 | [20.75, 20.75] | [30.03, 30.03] | [10.53, 10.53] | [2.0, 2.0] | 0 | 589.8 | 61.31 | 61.31 | 0 | 7.1 | 82 | 75 | 22.2 | 9.32 | 18.99 | 3.89 | 9.18 | 3463.49 | 1036.72 | 1308.11 | 755.04 | 30.62 | 1.66 | 4.29 | 70.54 | 680 | 5900 | 84.1 | 0.59 | 10.29 | 235.39 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 416001.47 | 416001.47 | 20230204-163228_b5a51695-f7fc-43bc-b477-c4f3e78d5541 | 0
22.86 | 32.13 | 5423.4 | 7.61 | [19.72, 19.72] | [30.01, 30.01] | [10.07, 10.07] | [2.0, 2.0] | 0 | 576.02 | 59.8 | 59.8 | 0 | 7.08 | 82 | 77 | 21.8 | 9.26 | 18.87 | 4 | 9.42 | 3470.98 | 1038.73 | 1312.85 | 756.52 | 29.91 | 1.66 | 4.29 | 69.86 | 680 | 5900 | 83.61 | 0.59 | 9.94 | 235.68 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 414437.46 | 414437.46 | 20230204-163228_34a68c8f-5108-4dd4-9e08-83271423bc71 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.46 | 31.35 | 5470.5 | 7.61 | [21.82, 21.82] | [30.04, 30.04] | [5.65, 5.65] | [2.0, 2.0] | 0 | 631.97 | 57.51 | 57.51 | 0 | 7.04 | 81.95 | 87 | 20 | 8.89 | 18.4 | 4.06 | 8.66 | 3501.12 | 1034.93 | 1217.28 | 731.74 | 28.8 | 1.61 | 4.38 | 68.65 | 680 | 5900 | 80.25 | 0.59 | 10.48 | 235.98 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 412807.49 | 412807.49 | 20230204-163228_8e3e2b9d-9802-44f5-9363-e1daa40f923d | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21.75 | 29.98 | 5536.1 | 7.59 | [21.43, 21.43] | [30.18, 30.18] | [2.56, 2.56] | [3.44, 3.44] | 0 | 642.99 | 54.17 | 54.17 | 0 | 6.97 | 82 | 94 | 18.7 | 8.24 | 17.97 | 3.77 | 8.61 | 3543.1 | 1039.04 | 1169.07 | 720.91 | 15.77 | 1.57 | 4.45 | 68.58 | 680 | 5900 | 74.35 | 0.59 | 9.77 | 137.15 | 60 | 9 | 9 | 0.23 | 408 | 410.06 | 426037.18 | 426037.18 | 20230204-163228_ab778cfe-e213-44de-aaf0-af4f25431fe8 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.66 | 31.87 | 5447 | 7.61 | [16.56, 16.56] | [30.01, 30.01] | [9.7, 9.7] | [2.0, 2.0] | 0 | 523.69 | 56.27 | 56.27 | 0 | 7.03 | 82.09 | 82 | 20.7 | 9.21 | 18.45 | 4.21 | 10.4 | 3486.08 | 1045.61 | 1351.21 | 766.98 | 28.12 | 1.67 | 4.27 | 68.63 | 680 | 5900 | 83.13 | 0.59 | 8.84 | 235.48 | 60 | 9 | 9 | 0.13 | 408 | 409.2 | 411357.01 | 411357.01 | 20230204-163228_232f0df2-d2fd-4d6a-9561-76ac96f8409f | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## P2
supply_temp | return_temp | ct_conductivity | ct_ph | Bore | CWRO | BoilrBD | BD | scheme | mu_conductivity | mu_flow(PV) | mu-flow(Ov) | mu-saving(PV-OV) | mu_ph | cooling_tower_level | relative_humidity | ambient_temp | delta_temp | wetBulb_temp | approach_temp | cond_coc | ct_tds | ct_ca | ct_alk | ct_chloride | flow_cycle | sat_index | sta_index | perf_index | system_vol | rec_rate | evap_loss | drift_loss | blowdown_coc | hold_time_index | dosing_residual | dosing_contact_time | dosing_density | dosing_continuous | dosing_initial | dosing_slug | currentOperatingCost | newOperatingCost | updatedDateTime | 609.3024
0 | 6 | 80.89 | 7.8 | [0.0, 0.0] | [17.16, 17.16] | [0.0, 0.0] | [3.61, 3.61] | 0 | 35 | 17.16 | 17.16 | 0 | 6.3 | 0 | 44 | 22.5 | 6 | 14.96 | -14.96 | 2.31 | 51.77 | 11.79 | 28.19 | 6.47 | 4.75 | -2.04 | 11.87 | -66.93 | 160 | 1460 | 13.4 | 0.15 | 10.22 | 30.73 | 60 | 9 | 9 | 0.24 | 96 | 98.17 | 247082.33 | 247082.33 | 20230204-160652_2002ecfe-bd5b-4d66-b73c-bc6b1d75d014 | 0
0 | 6 | 100.04 | 7.8 | [0.0, 0.0] | [16.12, 16.12] | [0.0, 0.0] | [2.58, 2.58] | 0 | 35 | 16.12 | 16.12 | 0 | 6.3 | 0 | 46 | 21.7 | 6 | 14.59 | -14.59 | 2.86 | 64.02 | 14.58 | 34.87 | 8 | 6.26 | -1.86 | 11.52 | -69.85 | 160 | 1460 | 13.4 | 0.15 | 7.21 | 43.05 | 60 | 9 | 9 | 0.17 | 96 | 97.55 | 223917.86 | 223917.86 | 20230204-160652_99555fc7-8c3b-4882-a6f7-4504d0b92880 | 0
0 | 6 | 73.44 | 7.8 | [0.0, 0.92] | [17.85, 13.36] | [0.0, 0.0] | [4.3, 0.73] | 0 | 35 | 17.85 | 14.28 | 3.57 | 6.3 | 0 | 63 | 19.9 | 6 | 15.3 | -15.3 | 2.1 | 47 | 10.7 | 25.6 | 5.88 | 24.38 | -2.12 | 12.03 | -64.49 | 160 | 1460 | 13.4 | 0.15 | 12.2 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 262694.34 | 172101.2 | 20230204-160652_112b7c4b-48f6-4fee-9835-c897f50db736 | 5.1708
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 77.39 | 7.8 | [0.0, 0.0] | [17.45, 17.45] | [0.0, 0.0] | [3.9, 3.9] | 0 | 35 | 17.45 | 17.45 | 0 | 6.3 | 0 | 63 | 19.6 | 6 | 15.03 | -15.03 | 2.21 | 49.53 | 11.28 | 26.98 | 6.19 | 4.47 | -2.07 | 11.95 | -66.44 | 160 | 1460 | 13.4 | 0.15 | 11.07 | 28.41 | 60 | 9 | 9 | 0.26 | 96 | 98.34 | 253672.56 | 253672.56 | 20230204-160652_fab0dbb8-028f-4138-acb0-0f679b3742bd | 0
0 | 6 | 198.92 | 7.8 | [0.0, 0.92] | [14.61, 13.36] | [0.0, 0.0] | [1.06, 0.73] | 0 | 35 | 14.61 | 14.28 | 0.33 | 6.3 | 0 | 68 | 17.8 | 6 | 13.99 | -13.99 | 5.68 | 127.31 | 28.99 | 69.34 | 15.91 | 19.95 | -1.29 | 10.39 | -75.07 | 160 | 1460 | 13.4 | 0.15 | 2.86 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 189989.69 | 172101.2 | 20230204-160652_6eb5ef77-735c-4259-917e-f1e351772977 | 1.021
0 | 6 | 68.32 | 7.8 | [0.0, 0.0] | [18.54, 18.54] | [0.0, 0.0] | [4.99, 4.99] | 0 | 35 | 18.54 | 18.54 | 0 | 6.3 | 0 | 56 | 20.9 | 6 | 15.29 | -15.29 | 1.95 | 43.72 | 9.95 | 23.81 | 5.47 | 3.71 | -2.18 | 12.15 | -64.6 | 160 | 1460 | 13.4 | 0.15 | 14.08 | 22.21 | 60 | 9 | 9 | 0.33 | 96 | 99 | 278120.96 | 278120.96 | 20230204-160652_d3ca2bbe-cc61-4fde-8bfc-9ffe281ed7a3 | 0
0 | 6 | 67.5 | 7.8 | [0.0, 0.92] | [18.68, 13.36] | [0.0, 0.0] | [5.13, 0.73] | 0 | 35 | 18.68 | 14.28 | 4.4 | 6.3 | 0 | 50 | 21.9 | 6 | 15.33 | -15.33 | 1.93 | 43.2 | 9.84 | 23.53 | 5.4 | 25.5 | -2.19 | 12.17 | -64.29 | 160 | 1460 | 13.4 | 0.15 | 14.44 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 281141.71 | 172101.2 | 20230204-160652_270e0bcf-5337-4ce8-af48-c8601e639e04 | 6.2238
0 | 6 | 121.92 | 7.8 | [0.0, 0.0] | [15.5, 15.5] | [0.0, 0.0] | [1.95, 1.95] | 0 | 35 | 15.5 | 15.5 | 0 | 6.3 | 0 | 49 | 20.8 | 6 | 14.25 | -14.25 | 3.48 | 78.03 | 17.77 | 42.5 | 9.75 | 7.94 | -1.7 | 11.2 | -72.73 | 160 | 1460 | 13.4 | 0.15 | 5.4 | 56.79 | 60 | 9 | 9 | 0.13 | 96 | 97.17 | 209944.53 | 209944.53 | 20230204-160652_39b8955b-2c79-4917-ac03-a0880fdbbd46 | 0
0 | 6 | 69.43 | 7.8 | [0.0, 0.92] | [18.37, 13.36] | [0.0, 0.0] | [4.82, 0.73] | 0 | 35 | 18.37 | 14.28 | 4.09 | 6.3 | 0 | 47 | 22.2 | 6 | 15.16 | -15.16 | 1.98 | 44.44 | 10.12 | 24.2 | 5.55 | 25.08 | -2.16 | 12.13 | -65.52 | 160 | 1460 | 13.4 | 0.15 | 13.62 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 274307.88 | 172101.2 | 20230204-160652_c45e770a-13ee-47de-8283-022dba0e284a | 5.8337
0 | 6 | 109.25 | 7.8 | [0.0, 0.92] | [15.82, 13.36] | [0.0, 0.0] | [2.27, 0.73] | 0 | 35 | 15.82 | 14.28 | 1.54 | 6.3 | 0 | 65 | 18.4 | 6 | 14.18 | -14.18 | 3.12 | 69.92 | 15.92 | 38.08 | 8.74 | 21.6 | -1.79 | 11.38 | -73.32 | 160 | 1460 | 13.4 | 0.15 | 6.32 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 217048.81 | 172101.2 | 20230204-160652_d36adc95-942a-49a8-bced-44922c013e5e | 2.5655
0 | 6 | 69.21 | 7.8 | [0.0, 0.0] | [18.4, 18.4] | [0.0, 0.0] | [4.85, 4.85] | 0 | 35 | 18.4 | 18.4 | 0 | 6.3 | 0 | 62 | 20.3 | 6 | 15.54 | -15.54 | 1.98 | 44.29 | 10.08 | 24.12 | 5.54 | 3.79 | -2.17 | 12.13 | -62.91 | 160 | 1460 | 13.4 | 0.15 | 13.71 | 22.84 | 60 | 9 | 9 | 0.32 | 96 | 98.91 | 275038.58 | 275038.58 | 20230204-160652_0e42a183-e08c-4610-b39f-fa7f74843969 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 93.64 | 7.8 | [0.0, 0.92] | [16.39, 13.36] | [0.0, 0.0] | [2.84, 0.73] | 0 | 35 | 16.39 | 14.28 | 2.11 | 6.3 | 0 | 64 | 18.8 | 6 | 14.43 | -14.43 | 2.68 | 59.93 | 13.64 | 32.64 | 7.49 | 22.38 | -1.92 | 11.63 | -71.2 | 160 | 1460 | 13.4 | 0.15 | 8 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 229950.88 | 172101.2 | 20230204-160652_5abd403a-d726-45f8-b7e4-b4cdbe6cc1a9 | 3.3019
0 | 6 | 68.63 | 7.8 | [0.0, 0.92] | [18.49, 13.36] | [0.0, 0.0] | [4.94, 0.73] | 0 | 35 | 18.49 | 14.28 | 4.21 | 6.3 | 0 | 53 | 21.4 | 6 | 15.32 | -15.32 | 1.96 | 43.92 | 10 | 23.92 | 5.49 | 25.25 | -2.17 | 12.15 | -64.38 | 160 | 1460 | 13.4 | 0.15 | 13.95 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 277026.99 | 172101.2 | 20230204-160652_4eff511c-025f-4e1b-9331-9f4deb00d65a | 5.9889
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 77.42 | 7.8 | [0.0, 0.92] | [17.45, 13.36] | [0.0, 0.0] | [3.9, 0.73] | 0 | 35 | 17.45 | 14.28 | 3.17 | 6.3 | 0 | 44 | 22.6 | 6 | 15.05 | -15.05 | 2.21 | 49.55 | 11.28 | 26.98 | 6.19 | 23.82 | -2.07 | 11.95 | -66.32 | 160 | 1460 | 13.4 | 0.15 | 11.06 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 253618.2 | 172101.2 | 20230204-160652_c5c6454b-51a1-4fda-aa0d-529316b48465 | 4.6528
0 | 6 | 110.61 | 7.8 | [0.0, 0.92] | [15.78, 13.36] | [0.0, 0.0] | [2.23, 0.73] | 0 | 35 | 15.78 | 14.28 | 1.5 | 6.3 | 0 | 48 | 21 | 6 | 14.28 | -14.28 | 3.16 | 70.79 | 16.12 | 38.56 | 8.85 | 21.54 | -1.78 | 11.36 | -72.45 | 160 | 1460 | 13.4 | 0.15 | 6.2 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 216170.52 | 172101.2 | 20230204-160652_43d4023c-0c77-4e81-b9d5-c8c178f24cb5 | 2.5154
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 87.26 | 7.8 | [0.0, 0.92] | [16.73, 13.36] | [0.0, 0.0] | [3.18, 0.73] | 0 | 35 | 16.73 | 14.28 | 2.45 | 6.3 | 0 | 45 | 22.2 | 6 | 14.86 | -14.86 | 2.49 | 55.84 | 12.71 | 30.42 | 6.98 | 22.84 | -1.97 | 11.75 | -67.7 | 160 | 1460 | 13.4 | 0.15 | 8.98 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 237448.13 | 172101.2 | 20230204-160652_326510b5-793c-4963-82db-7429b7c8d3f9 | 3.7298
0 | 6 | 139.49 | 7.8 | [0.0, 0.92] | [15.19, 13.36] | [0.0, 0.0] | [1.64, 0.73] | 0 | 35 | 15.19 | 14.28 | 0.91 | 6.3 | 0 | 66 | 18.1 | 6 | 14.03 | -14.03 | 3.99 | 89.27 | 20.33 | 48.62 | 11.16 | 20.74 | -1.59 | 10.98 | -74.73 | 160 | 1460 | 13.4 | 0.15 | 4.49 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 202884.15 | 172101.2 | 20230204-160652_93b80a35-d03b-42cf-8cf3-91bfa591a408 | 1.757
0 | 6 | 71.98 | 7.8 | [0.0, 0.0] | [18.03, 18.03] | [0.0, 0.0] | [4.48, 4.48] | 0 | 35 | 18.03 | 18.03 | 0 | 6.3 | 0 | 44 | 22.9 | 6 | 15.3 | -15.3 | 2.06 | 46.07 | 10.49 | 25.09 | 5.76 | 4.03 | -2.13 | 12.07 | -64.53 | 160 | 1460 | 13.4 | 0.15 | 12.68 | 24.76 | 60 | 9 | 9 | 0.3 | 96 | 98.69 | 266584.84 | 266584.84 | 20230204-160652_a2aa0c9a-f8b5-486a-af18-6b7e3297075c | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 71.03 | 7.8 | [0.0, 0.0] | [18.15, 18.15] | [0.0, 0.0] | [4.6, 4.6] | 0 | 35 | 18.15 | 18.15 | 0 | 6.3 | 0 | 46 | 22.2 | 6 | 15.01 | -15.01 | 2.03 | 45.46 | 10.35 | 24.76 | 5.68 | 3.95 | -2.14 | 12.09 | -66.59 | 160 | 1460 | 13.4 | 0.15 | 13.02 | 24.1 | 60 | 9 | 9 | 0.31 | 96 | 98.76 | 269324.09 | 269324.09 | 20230204-160652_7992da71-1662-43de-ae95-8d1b6fd30c32 | 0
0 | 6 | 371.04 | 7.8 | [0.0, 0.92] | [14.08, 13.36] | [0.0, 0.0] | [0.53, 0.73] | 0 | 35 | 14.08 | 14.28 | -0.2 | 6.3 | 0 | 68 | 17.8 | 6 | 13.99 | -13.99 | 10.6 | 237.47 | 54.07 | 129.34 | 29.68 | 19.22 | -0.78 | 9.36 | -75.07 | 160 | 1460 | 13.4 | 0.15 | 1.4 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 178015.63 | 172101.2 | 20230204-160652_a922fd44-3964-4aa1-8c28-94ef9c927970 | 0.33758
0 | 6 | 82.68 | 7.8 | [0.0, 0.0] | [17.02, 17.02] | [0.0, 0.0] | [3.48, 3.48] | 0 | 35 | 17.02 | 17.02 | 0 | 6.3 | 0 | 63 | 19.3 | 6 | 14.76 | -14.76 | 2.36 | 52.92 | 12.05 | 28.82 | 6.61 | 4.9 | -2.02 | 11.84 | -68.51 | 160 | 1460 | 13.4 | 0.15 | 9.84 | 31.91 | 60 | 9 | 9 | 0.23 | 96 | 98.09 | 244095.97 | 244095.97 | 20230204-160652_21b5fbc6-6c83-4713-9b12-4d34ca9034c0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 163.24 | 7.8 | [0.0, 0.92] | [14.89, 13.36] | [0.0, 0.0] | [1.35, 0.73] | 0 | 35 | 14.89 | 14.28 | 0.61 | 6.3 | 0 | 70 | 22.6 | 6 | 18.7 | -18.7 | 4.66 | 104.47 | 23.79 | 56.9 | 13.06 | 20.34 | -1.46 | 10.72 | -47.24 | 160 | 1460 | 13.4 | 0.15 | 3.66 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 196340.67 | 172101.2 | 20230204-161315_c18632b4-4ec0-4111-9546-4b496a50f4e3 | 1.3835
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 181.32 | 7.8 | [0.0, 0.0] | [14.73, 14.73] | [0.0, 0.0] | [1.19, 1.19] | 0 | 35 | 14.73 | 14.73 | 0 | 6.3 | 0 | 81 | 17.8 | 6 | 15.54 | -15.54 | 5.18 | 116.05 | 26.42 | 63.2 | 14.51 | 12.43 | -1.37 | 10.54 | -62.92 | 160 | 1460 | 13.4 | 0.15 | 3.21 | 93.54 | 60 | 9 | 9 | 0.08 | 96 | 96.71 | 192746.63 | 192746.63 | 20230204-161315_337ac0c4-cca7-4eb2-ae61-2531d62b51af | 0
0 | 6 | 160.37 | 7.8 | [0.0, 0.92] | [14.92, 13.36] | [0.0, 0.0] | [1.38, 0.73] | 0 | 35 | 14.92 | 14.28 | 0.64 | 6.3 | 0 | 76 | 19.9 | 6 | 16.94 | -16.94 | 4.58 | 102.64 | 23.37 | 55.9 | 12.83 | 20.38 | -1.47 | 10.75 | -54.86 | 160 | 1460 | 13.4 | 0.15 | 3.74 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 197002.85 | 172101.2 | 20230204-161315_020ccc41-143d-4620-b7f7-e36c202f57e7 | 1.4213
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 133.13 | 7.8 | [0.0, 0.92] | [15.29, 13.36] | [0.0, 0.0] | [1.74, 0.73] | 0 | 35 | 15.29 | 14.28 | 1.01 | 6.3 | 0 | 78 | 21.6 | 6 | 18.81 | -18.81 | 3.8 | 85.21 | 19.4 | 46.41 | 10.65 | 20.87 | -1.63 | 11.05 | -46.85 | 160 | 1460 | 13.4 | 0.15 | 4.78 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 205152.94 | 172101.2 | 20230204-161315_44539f67-e12a-4365-a761-45da7ef788f4 | 1.8865
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 286.89 | 7.8 | [0.0, 0.92] | [14.25, 13.36] | [0.0, 0.0] | [0.7, 0.73] | 0 | 35 | 14.25 | 14.28 | -0.03 | 6.3 | 0 | 84 | 16.5 | 6 | 14.63 | -14.63 | 8.2 | 183.61 | 41.8 | 100 | 22.95 | 19.46 | -0.99 | 9.79 | -69.53 | 160 | 1460 | 13.4 | 0.15 | 1.86 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 181871.25 | 172101.2 | 20230204-161315_90fcb8fb-987a-45e6-86ab-f76005e7639b | 0.55765
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 141.13 | 7.8 | [0.0, 0.92] | [15.16, 13.36] | [0.0, 0.0] | [1.61, 0.73] | 0 | 35 | 15.16 | 14.28 | 0.88 | 6.3 | 0 | 74 | 21.5 | 6 | 18.2 | -18.2 | 4.03 | 90.32 | 20.56 | 49.19 | 11.29 | 20.7 | -1.58 | 10.96 | -49.19 | 160 | 1460 | 13.4 | 0.15 | 4.42 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 202340.8 | 172101.2 | 20230204-161315_8eee0256-59bc-4ce3-a30a-5382b8e20255 | 1.726
0 | 6 | 133.2 | 7.8 | [0.0, 0.0] | [15.29, 15.29] | [0.0, 0.0] | [1.74, 1.74] | 0 | 35 | 15.29 | 15.29 | 0 | 6.3 | 0 | 77 | 21.4 | 6 | 18.49 | -18.49 | 3.81 | 85.25 | 19.41 | 46.43 | 10.66 | 8.8 | -1.63 | 11.05 | -48.04 | 160 | 1460 | 13.4 | 0.15 | 4.78 | 63.82 | 60 | 9 | 9 | 0.12 | 96 | 97.04 | 205127.15 | 205127.15 | 20230204-161315_5e25c133-a876-4251-b978-b5a07e0a77bd | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 109.46 | 7.8 | [0.0, 0.92] | [15.81, 13.36] | [0.0, 0.0] | [2.26, 0.73] | 0 | 35 | 15.81 | 14.28 | 1.53 | 6.3 | 0 | 63 | 23.1 | 6 | 18.21 | -18.21 | 3.13 | 70.05 | 15.95 | 38.15 | 8.76 | 21.59 | -1.79 | 11.38 | -49.13 | 160 | 1460 | 13.4 | 0.15 | 6.3 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 216910.97 | 172101.2 | 20230204-161315_74a80635-e644-4046-9984-5c01f8576e73 | 2.5576
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 290.24 | 7.8 | [0.0, 0.92] | [14.24, 13.36] | [0.0, 0.0] | [0.69, 0.73] | 0 | 35 | 14.24 | 14.28 | -0.04 | 6.3 | 0 | 86 | 16 | 6 | 14.37 | -14.37 | 8.29 | 185.76 | 42.29 | 101.17 | 23.22 | 19.44 | -0.98 | 9.77 | -71.66 | 160 | 1460 | 13.4 | 0.15 | 1.84 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 181670.15 | 172101.2 | 20230204-161315_d2524044-50c0-471e-9160-5ca0a60c9f8e | 0.54617
0 | 6 | 126.07 | 7.8 | [0.0, 0.92] | [15.42, 13.36] | [0.0, 0.0] | [1.87, 0.73] | 0 | 35 | 15.42 | 14.28 | 1.14 | 6.3 | 0 | 61 | 23 | 6 | 17.84 | -17.84 | 3.6 | 80.69 | 18.37 | 43.95 | 10.09 | 21.05 | -1.67 | 11.14 | -50.66 | 160 | 1460 | 13.4 | 0.15 | 5.15 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 208035.21 | 172101.2 | 20230204-161315_6230373d-14ce-422d-8422-db746e92b142 | 2.051
0 | 6 | 189.88 | 7.8 | [0.0, 0.0] | [14.67, 14.67] | [0.0, 0.0] | [1.12, 1.12] | 0 | 35 | 14.67 | 14.67 | 0 | 6.3 | 0 | 84 | 16.8 | 6 | 14.92 | -14.92 | 5.43 | 121.52 | 27.67 | 66.19 | 15.19 | 13.07 | -1.33 | 10.47 | -67.26 | 160 | 1460 | 13.4 | 0.15 | 3.03 | 98.8 | 60 | 9 | 9 | 0.07 | 96 | 96.67 | 191330.11 | 191330.11 | 20230204-161315_0ef14bcd-df90-453b-922f-49d6953fa13e | 0
0 | 6 | 133.57 | 7.8 | [0.0, 0.92] | [15.28, 13.36] | [0.0, 0.0] | [1.73, 0.73] | 0 | 35 | 15.28 | 14.28 | 1 | 6.3 | 0 | 73 | 21.2 | 6 | 17.79 | -17.79 | 3.82 | 85.49 | 19.46 | 46.56 | 10.69 | 20.86 | -1.62 | 11.05 | -50.91 | 160 | 1460 | 13.4 | 0.15 | 4.76 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 204986.64 | 172101.2 | 20230204-161315_db37e0d8-9ac0-4cc2-b48e-c9dca0847f67 | 1.877
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 194.92 | 7.8 | [0.0, 0.92] | [14.64, 13.36] | [0.0, 0.0] | [1.09, 0.73] | 0 | 35 | 14.64 | 14.28 | 0.36 | 6.3 | 0 | 78 | 18.9 | 6 | 16.23 | -16.23 | 5.57 | 124.75 | 28.4 | 67.94 | 15.59 | 19.99 | -1.31 | 10.42 | -58.65 | 160 | 1460 | 13.4 | 0.15 | 2.93 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 190564.65 | 172101.2 | 20230204-161315_4fac19bf-be0e-4830-b177-06b8b932ab9b | 1.0538
0 | 6 | 78.54 | 7.8 | [0.0, 0.92] | [17.35, 13.36] | [0.0, 0.0] | [3.8, 0.73] | 0 | 35 | 17.35 | 14.28 | 3.07 | 6.3 | 0 | 63 | 22.9 | 6 | 18.03 | -18.03 | 2.24 | 50.27 | 11.44 | 27.38 | 6.28 | 23.69 | -2.06 | 11.92 | -49.87 | 160 | 1460 | 13.4 | 0.15 | 10.77 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 251375.42 | 172101.2 | 20230204-161940_b5aa3c25-f98c-4548-a6bd-aefc752f69df | 4.5248
0 | 6 | 154.14 | 7.8 | [0.0, 0.92] | [14.99, 13.36] | [0.0, 0.0] | [1.44, 0.73] | 0 | 35 | 14.99 | 14.28 | 0.71 | 6.3 | 0 | 89 | 20.2 | 6 | 18.84 | -18.84 | 4.4 | 98.65 | 22.46 | 53.73 | 12.33 | 20.47 | -1.51 | 10.81 | -46.72 | 160 | 1460 | 13.4 | 0.15 | 3.94 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 198549.06 | 172101.2 | 20230204-161940_5215ea75-d554-4ddf-8c6c-29b51d7b9639 | 1.5096
0 | 6 | 77.63 | 7.8 | [0.0, 0.92] | [17.43, 13.36] | [0.0, 0.0] | [3.88, 0.73] | 0 | 35 | 17.43 | 14.28 | 3.15 | 6.3 | 0 | 89 | 19.9 | 6 | 18.55 | -18.55 | 2.22 | 49.68 | 11.31 | 27.06 | 6.21 | 23.8 | -2.07 | 11.94 | -47.82 | 160 | 1460 | 13.4 | 0.15 | 11 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 253189.27 | 172101.2 | 20230204-161940_669a4f16-6e26-47c3-bd3d-f0b3d1d0b95e | 4.6283
0 | 6 | 91.79 | 7.8 | [0.0, 0.0] | [16.48, 16.48] | [0.0, 0.0] | [2.93, 2.93] | 0 | 35 | 16.48 | 16.48 | 0 | 6.3 | 0 | 83 | 20.8 | 6 | 18.68 | -18.68 | 2.62 | 58.75 | 13.38 | 32 | 7.34 | 5.62 | -1.93 | 11.67 | -47.33 | 160 | 1460 | 13.4 | 0.15 | 8.26 | 37.8 | 60 | 9 | 9 | 0.2 | 96 | 97.76 | 231944.51 | 231944.51 | 20230204-161940_1696e315-f61f-4157-9758-68c416da3ba7 | 0
0 | 6 | 135.6 | 7.8 | [0.0, 0.92] | [15.25, 13.36] | [0.0, 0.0] | [1.7, 0.73] | 0 | 35 | 15.25 | 14.28 | 0.97 | 6.3 | 0 | 94 | 19 | 6 | 18.27 | -18.27 | 3.87 | 86.79 | 19.76 | 47.27 | 10.85 | 20.82 | -1.61 | 11.02 | -48.89 | 160 | 1460 | 13.4 | 0.15 | 4.66 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 204238.08 | 172101.2 | 20230204-161940_5ccf4030-eb78-4992-aaa0-f37b239fc28f | 1.8343
0 | 6 | 145.24 | 7.8 | [0.0, 0.92] | [15.1, 13.36] | [0.0, 0.0] | [1.56, 0.73] | 0 | 35 | 15.1 | 14.28 | 0.82 | 6.3 | 0 | 94 | 19.5 | 6 | 18.77 | -18.77 | 4.15 | 92.96 | 21.16 | 50.63 | 11.62 | 20.62 | -1.55 | 10.91 | -46.99 | 160 | 1460 | 13.4 | 0.15 | 4.26 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 201047.03 | 172101.2 | 20230204-161940_8298a46e-ef95-4a25-9f54-4b055c90b1fd | 1.6522
0 | 6 | 88.6 | 7.8 | [0.0, 0.92] | [16.65, 13.36] | [0.0, 0.0] | [3.1, 0.73] | 0 | 35 | 16.65 | 14.28 | 2.37 | 6.3 | 0 | 84 | 20.7 | 6 | 18.71 | -18.71 | 2.53 | 56.7 | 12.91 | 30.88 | 7.09 | 22.74 | -1.96 | 11.72 | -47.22 | 160 | 1460 | 13.4 | 0.15 | 8.75 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 235723.8 | 172101.2 | 20230204-161940_a2738943-0b03-446e-b973-af40f204db84 | 3.6314
0 | 6 | 108.08 | 7.8 | [0.0, 0.92] | [15.85, 13.36] | [0.0, 0.0] | [2.3, 0.73] | 0 | 35 | 15.85 | 14.28 | 1.57 | 6.3 | 0 | 97 | 17.7 | 6 | 17.34 | -17.34 | 3.09 | 69.17 | 15.75 | 37.67 | 8.65 | 21.65 | -1.8 | 11.4 | -52.93 | 160 | 1460 | 13.4 | 0.15 | 6.42 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 217827.22 | 172101.2 | 20230204-161940_f5f80809-4d1f-4fc5-b958-c04a0e03ef20 | 2.6099
0 | 6 | 73.17 | 7.8 | [0.0, 0.92] | [17.88, 13.36] | [0.0, 0.0] | [4.34, 0.73] | 0 | 35 | 17.88 | 14.28 | 3.6 | 6.3 | 0 | 77 | 21.2 | 6 | 18.3 | -18.3 | 2.09 | 46.83 | 10.66 | 25.51 | 5.85 | 24.42 | -2.12 | 12.04 | -48.79 | 160 | 1460 | 13.4 | 0.15 | 12.29 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 263390.05 | 172101.2 | 20230204-161940_71363234-a300-4312-9579-39e8b34096b7 | 5.2106
0 | 6 | 94.23 | 7.8 | [0.0, 0.92] | [16.37, 13.36] | [0.0, 0.0] | [2.82, 0.73] | 0 | 35 | 16.37 | 14.28 | 2.09 | 6.3 | 0 | 61 | 23 | 6 | 17.84 | -17.84 | 2.69 | 60.31 | 13.73 | 32.85 | 7.54 | 22.35 | -1.91 | 11.62 | -50.66 | 160 | 1460 | 13.4 | 0.15 | 7.92 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 229339.01 | 172101.2 | 20230204-161940_55fd6eec-b5c6-42ff-94f0-3f6212519031 | 3.267
0 | 6 | 80.82 | 7.8 | [0.0, 0.92] | [17.16, 13.36] | [0.0, 0.0] | [3.61, 0.73] | 0 | 35 | 17.16 | 14.28 | 2.88 | 6.3 | 0 | 66 | 22.6 | 6 | 18.16 | -18.16 | 2.31 | 51.73 | 11.78 | 28.17 | 6.47 | 23.43 | -2.04 | 11.88 | -49.32 | 160 | 1460 | 13.4 | 0.15 | 10.24 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 247187.04 | 172101.2 | 20230204-161940_7f7d2fa2-4db7-4bfc-a70a-bf94d004b1c4 | 4.2857
0 | 6 | 97.23 | 7.8 | [0.0, 0.92] | [16.24, 13.36] | [0.0, 0.0] | [2.69, 0.73] | 0 | 35 | 16.24 | 14.28 | 1.96 | 6.3 | 0 | 84 | 20.9 | 6 | 18.9 | -18.9 | 2.78 | 62.23 | 14.17 | 33.89 | 7.78 | 22.17 | -1.89 | 11.57 | -46.51 | 160 | 1460 | 13.4 | 0.15 | 7.54 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 226408.39 | 172101.2 | 20230204-161940_6bb85cae-d577-4efa-9e80-71e64d32fdac | 3.0997
0 | 6 | 168.73 | 7.8 | [0.0, 0.92] | [14.84, 13.36] | [0.0, 0.0] | [1.29, 0.73] | 0 | 35 | 14.84 | 14.28 | 0.56 | 6.3 | 0 | 91 | 19.6 | 6 | 18.5 | -18.5 | 4.82 | 107.98 | 24.59 | 58.81 | 13.5 | 20.27 | -1.43 | 10.66 | -48 | 160 | 1460 | 13.4 | 0.15 | 3.51 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 195150.63 | 172101.2 | 20230204-161940_330582db-8de1-4789-af78-f5c23e0515fd | 1.3156
0 | 6 | 96.45 | 7.8 | [0.0, 0.92] | [16.27, 13.36] | [0.0, 0.0] | [2.72, 0.73] | 0 | 35 | 16.27 | 14.28 | 1.99 | 6.3 | 0 | 62 | 23.3 | 6 | 18.25 | -18.25 | 2.76 | 61.73 | 14.05 | 33.62 | 7.72 | 22.21 | -1.89 | 11.58 | -48.96 | 160 | 1460 | 13.4 | 0.15 | 7.63 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 227143.07 | 172101.2 | 20230204-161940_4e8d8934-b950-42ab-91de-02eab0731f3f | 3.1417
0 | 6 | 75.6 | 7.8 | [0.0, 0.92] | [17.62, 13.36] | [0.0, 0.0] | [4.07, 0.73] | 0 | 35 | 17.62 | 14.28 | 3.34 | 6.3 | 0 | 84 | 20.5 | 6 | 18.51 | -18.51 | 2.16 | 48.38 | 11.02 | 26.35 | 6.05 | 24.06 | -2.09 | 11.99 | -47.96 | 160 | 1460 | 13.4 | 0.15 | 11.55 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 257527.95 | 172101.2 | 20230204-161940_49b0d643-eca4-4310-95e9-df8668edea2c | 4.876
0 | 6 | 75.26 | 7.8 | [0.0, 0.92] | [17.66, 13.36] | [0.0, 0.0] | [4.11, 0.73] | 0 | 35 | 17.66 | 14.28 | 3.38 | 6.3 | 0 | 89 | 19.4 | 6 | 18.06 | -18.06 | 2.15 | 48.16 | 10.97 | 26.23 | 6.02 | 24.11 | -2.1 | 11.99 | -49.77 | 160 | 1460 | 13.4 | 0.15 | 11.65 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 258303.64 | 172101.2 | 20230204-161940_b8b608f7-a603-484a-8c2a-a4d159c353b0 | 4.9202
0 | 6 | 136.69 | 7.8 | [0.0, 0.0] | [15.23, 15.23] | [0.0, 0.0] | [1.68, 1.68] | 0 | 35 | 15.23 | 15.23 | 0 | 6.3 | 0 | 92 | 19.1 | 6 | 18.13 | -18.13 | 3.91 | 87.48 | 19.92 | 47.65 | 10.94 | 9.06 | -1.6 | 11.01 | -49.48 | 160 | 1460 | 13.4 | 0.15 | 4.61 | 65.98 | 60 | 9 | 9 | 0.11 | 96 | 97.01 | 203847.3 | 203847.3 | 20230204-161940_b098edc8-b0f1-4c75-a2af-7f67c5b1a006 | 0
0 | 6 | 115.78 | 7.8 | [0.0, 0.92] | [15.64, 13.36] | [0.0, 0.0] | [2.09, 0.73] | 0 | 35 | 15.64 | 14.28 | 1.36 | 6.3 | 0 | 97 | 17.3 | 6 | 16.94 | -16.94 | 3.31 | 74.1 | 16.87 | 40.36 | 9.26 | 21.36 | -1.74 | 11.28 | -54.87 | 160 | 1460 | 13.4 | 0.15 | 5.81 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 213116.01 | 172101.2 | 20230204-161940_78126632-cfb1-4c76-bca9-725a05622f37 | 2.341
0 | 6 | 101.65 | 7.8 | [0.0, 0.92] | [16.06, 13.36] | [0.0, 0.0] | [2.52, 0.73] | 0 | 35 | 16.06 | 14.28 | 1.78 | 6.3 | 0 | 83 | 20.6 | 6 | 18.48 | -18.48 | 2.9 | 65.06 | 14.81 | 35.43 | 8.13 | 21.93 | -1.85 | 11.5 | -48.07 | 160 | 1460 | 13.4 | 0.15 | 7.04 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 222576.23 | 172101.2 | 20230204-161940_d0654960-d4a8-4ebf-89e8-4ef79766dafd | 2.881
0 | 6 | 127.31 | 7.8 | [0.0, 0.0] | [15.39, 15.39] | [0.0, 0.0] | [1.84, 1.84] | 0 | 35 | 15.39 | 15.39 | 0 | 6.3 | 0 | 95 | 18.6 | 6 | 17.99 | -17.99 | 3.64 | 81.48 | 18.55 | 44.38 | 10.19 | 8.35 | -1.66 | 11.13 | -50.02 | 160 | 1460 | 13.4 | 0.15 | 5.08 | 60.16 | 60 | 9 | 9 | 0.12 | 96 | 97.11 | 207497.44 | 207497.44 | 20230204-161940_24999d64-ae9a-4bf1-9e01-545f40a200af | 0
0 | 6 | 159.35 | 7.8 | [0.0, 0.92] | [14.93, 13.36] | [0.0, 0.0] | [1.39, 0.73] | 0 | 35 | 14.93 | 14.28 | 0.65 | 6.3 | 0 | 90 | 19.4 | 6 | 18.18 | -18.18 | 4.55 | 101.99 | 23.22 | 55.55 | 12.75 | 20.39 | -1.48 | 10.76 | -49.27 | 160 | 1460 | 13.4 | 0.15 | 3.77 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 197244.92 | 172101.2 | 20230204-161940_55dd3712-5842-40af-bdac-f0237564dada | 1.4351
0 | 6 | 116.64 | 7.8 | [0.0, 0.92] | [15.62, 13.36] | [0.0, 0.0] | [2.07, 0.73] | 0 | 35 | 15.62 | 14.28 | 1.34 | 6.3 | 0 | 96 | 18.1 | 6 | 17.62 | -17.62 | 3.33 | 74.65 | 17 | 40.66 | 9.33 | 21.33 | -1.74 | 11.27 | -51.65 | 160 | 1460 | 13.4 | 0.15 | 5.75 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 212642.74 | 172101.2 | 20230204-161940_7f6e81ff-6745-494e-aae9-8fb1819f0153 | 2.314
0 | 6 | 107.75 | 7.8 | [0.0, 0.92] | [15.86, 13.36] | [0.0, 0.0] | [2.31, 0.73] | 0 | 35 | 15.86 | 14.28 | 1.58 | 6.3 | 0 | 88 | 20.1 | 6 | 18.62 | -18.62 | 3.08 | 68.96 | 15.7 | 37.56 | 8.62 | 21.66 | -1.8 | 11.4 | -47.54 | 160 | 1460 | 13.4 | 0.15 | 6.45 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 218050.35 | 172101.2 | 20230204-161940_b6524f31-8bbc-4434-a8eb-a220a1e50913 | 2.6227
0 | 6 | 171.99 | 7.8 | [0.0, 0.92] | [14.81, 13.36] | [0.0, 0.0] | [1.26, 0.73] | 0 | 35 | 14.81 | 14.28 | 0.53 | 6.3 | 0 | 90 | 19.6 | 6 | 18.38 | -18.38 | 4.91 | 110.07 | 25.06 | 59.95 | 13.76 | 20.22 | -1.41 | 10.63 | -48.48 | 160 | 1460 | 13.4 | 0.15 | 3.42 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 194487.47 | 172101.2 | 20230204-161940_f791e109-5949-460c-9ee6-75d59a50a7f3 | 1.2778
0 | 6 | 91.34 | 7.8 | [0.0, 0.0] | [16.5, 16.5] | [0.0, 0.0] | [2.96, 2.96] | 0 | 35 | 16.5 | 16.5 | 0 | 6.3 | 0 | 62 | 22.9 | 6 | 17.89 | -17.89 | 2.61 | 58.46 | 13.31 | 31.84 | 7.31 | 5.58 | -1.94 | 11.67 | -50.45 | 160 | 1460 | 13.4 | 0.15 | 8.33 | 37.51 | 60 | 9 | 9 | 0.2 | 96 | 97.77 | 232449.62 | 232449.62 | 20230204-161940_16b7d7f2-6364-44cd-b718-af28e797449f | 0
0 | 6 | 79.13 | 7.8 | [0.0, 0.92] | [17.3, 13.36] | [0.0, 0.0] | [3.75, 0.73] | 0 | 35 | 17.3 | 14.28 | 3.02 | 6.3 | 0 | 90 | 19.8 | 6 | 18.57 | -18.57 | 2.26 | 50.64 | 11.53 | 27.58 | 6.33 | 23.62 | -2.06 | 11.91 | -47.72 | 160 | 1460 | 13.4 | 0.15 | 10.63 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 250249.79 | 172101.2 | 20230204-161940_011fb6e1-ac91-412d-8071-8965b7627169 | 4.4605
0 | 6 | 96.24 | 7.8 | [0.0, 0.92] | [16.28, 13.36] | [0.0, 0.0] | [2.73, 0.73] | 0 | 35 | 16.28 | 14.28 | 2 | 6.3 | 0 | 97 | 16.9 | 6 | 16.54 | -16.54 | 2.75 | 61.59 | 14.02 | 33.55 | 7.7 | 22.23 | -1.89 | 11.59 | -56.95 | 160 | 1460 | 13.4 | 0.15 | 7.66 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 227343.33 | 172101.2 | 20230204-162602_6cb08677-e976-45ae-87db-f4548b79c838 | 3.1531
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 94.19 | 7.8 | [0.0, 0.0] | [16.37, 16.37] | [0.0, 0.0] | [2.82, 2.82] | 0 | 35 | 16.37 | 16.37 | 0 | 6.3 | 0 | 98 | 17.1 | 6 | 16.85 | -16.85 | 2.69 | 60.28 | 13.73 | 32.83 | 7.54 | 5.81 | -1.91 | 11.62 | -55.28 | 160 | 1460 | 13.4 | 0.15 | 7.93 | 39.34 | 60 | 9 | 9 | 0.19 | 96 | 97.69 | 229376.31 | 229376.31 | 20230204-162602_1ad30b17-4fbc-4f3e-a995-e7e0ad0ce9a1 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 85.83 | 7.8 | [0.0, 0.92] | [16.81, 13.36] | [0.0, 0.0] | [3.27, 0.73] | 0 | 35 | 16.81 | 14.28 | 2.53 | 6.3 | 0 | 98 | 16.8 | 6 | 16.55 | -16.55 | 2.45 | 54.93 | 12.51 | 29.92 | 6.87 | 22.96 | -1.99 | 11.78 | -56.86 | 160 | 1460 | 13.4 | 0.15 | 9.23 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 239394.58 | 172101.2 | 20230204-162602_8f298c37-cf64-402d-94f8-78d928747063 | 3.8409
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 159.28 | 7.8 | [0.0, 0.92] | [14.94, 13.36] | [0.0, 0.0] | [1.39, 0.73] | 0 | 35 | 14.94 | 14.28 | 0.66 | 6.3 | 0 | 98 | 16.6 | 6 | 16.35 | -16.35 | 4.55 | 101.94 | 23.21 | 55.52 | 12.74 | 20.39 | -1.48 | 10.76 | -57.96 | 160 | 1460 | 13.4 | 0.15 | 3.77 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 197263.42 | 172101.2 | 20230204-162602_59b604ee-f80e-429e-9f33-a8d2fe874ab9 | 1.4362
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 91.33 | 7.8 | [0.0, 0.92] | [16.51, 13.36] | [0.0, 0.0] | [2.96, 0.73] | 0 | 35 | 16.51 | 14.28 | 2.23 | 6.3 | 0 | 98 | 17.1 | 6 | 16.85 | -16.85 | 2.61 | 58.45 | 13.31 | 31.84 | 7.31 | 22.54 | -1.94 | 11.67 | -55.28 | 160 | 1460 | 13.4 | 0.15 | 8.33 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 232460.44 | 172101.2 | 20230204-162602_b4176341-9e94-4677-8a3b-64dc122428ec | 3.4452
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 144.63 | 7.8 | [0.0, 0.92] | [15.11, 13.36] | [0.0, 0.0] | [1.56, 0.73] | 0 | 35 | 15.11 | 14.28 | 0.83 | 6.3 | 0 | 78 | 22 | 6 | 19.19 | -19.19 | 4.13 | 92.56 | 21.07 | 50.41 | 11.57 | 20.64 | -1.56 | 10.92 | -45.49 | 160 | 1460 | 13.4 | 0.15 | 4.28 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 201235.19 | 172101.2 | 20230204-162602_1682a359-b710-4c8c-b165-638bbb24d498 | 1.6629
0 | 6 | 95.4 | 7.8 | [0.0, 0.92] | [16.31, 13.36] | [0.0, 0.0] | [2.76, 0.73] | 0 | 35 | 16.31 | 14.28 | 2.03 | 6.3 | 0 | 98 | 17 | 6 | 16.75 | -16.75 | 2.73 | 61.05 | 13.9 | 33.25 | 7.63 | 22.28 | -1.9 | 11.6 | -55.8 | 160 | 1460 | 13.4 | 0.15 | 7.77 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 228164.58 | 172101.2 | 20230204-162602_8e4c90e8-c938-4dbc-85f2-1b8b57d6a6ed | 3.2
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 74.46 | 7.8 | [0.0, 0.92] | [17.74, 13.36] | [0.0, 0.0] | [4.19, 0.73] | 0 | 35 | 17.74 | 14.28 | 3.46 | 6.3 | 0 | 96 | 19.5 | 6 | 19.01 | -19.01 | 2.13 | 47.65 | 10.85 | 25.95 | 5.96 | 24.22 | -2.11 | 12.01 | -46.1 | 160 | 1460 | 13.4 | 0.15 | 11.89 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 260180.16 | 172101.2 | 20230204-163228_9cadf07f-d77d-4cf3-9589-b1c2fd0c30fa | 5.0273
0 | 6 | 53.95 | 7.8 | [2.18, 0.92] | [24.1, 13.36] | [0.0, 0.0] | [12.74, 0.73] | 0 | 159.92 | 26.28 | 14.28 | 12 | 6.42 | 0 | 85 | 20.4 | 6 | 18.54 | -18.54 | 0.34 | 34.53 | 9.67 | 12.23 | 6.41 | 35.89 | -2.47 | 12.74 | -47.85 | 160 | 1460 | 13.4 | 0.15 | -20.23 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 426935.4 | 172101.2 | 20230204-163228_d4aac477-4f9f-441e-9337-757c6a96df4a | 14.5453
0 | 6 | 58.85 | 7.8 | [0.0, 0.0] | [20.97, 20.97] | [0.0, 0.0] | [7.42, 7.42] | 0 | 35 | 20.97 | 20.97 | 0 | 6.3 | 0 | 76 | 21.8 | 6 | 18.74 | -18.74 | 1.68 | 37.66 | 8.57 | 20.51 | 4.71 | 2.83 | -2.3 | 12.4 | -47.1 | 160 | 1460 | 13.4 | 0.15 | 19.67 | 14.95 | 60 | 9 | 9 | 0.49 | 96 | 100.45 | 332536.05 | 332536.05 | 20230204-163228_f4d9136d-7c5f-4115-bed5-81e02ade9b44 | 0
0 | 6 | 55.85 | 7.8 | [10.57, 0.92] | [22.64, 13.36] | [0.0, 0.0] | [19.66, 0.73] | 0 | 514 | 33.21 | 14.28 | 18.93 | 6.78 | 0 | 89 | 18.9 | 6 | 17.56 | -17.56 | 0.11 | 35.74 | 10.37 | 11.35 | 7.05 | 45.34 | -2.47 | 12.74 | -51.88 | 160 | 1460 | 13.4 | 0.15 | -15.04 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 486612.21 | 172101.2 | 20230204-163228_44f0f0bd-fd82-44c2-9d63-55e7a60fb289 | 17.9515
0 | 6 | 66.29 | 7.8 | [0.0, 0.0] | [18.89, 18.89] | [0.0, 0.0] | [5.34, 5.34] | 0 | 35 | 18.89 | 18.89 | 0 | 6.3 | 0 | 71 | 22.2 | 6 | 18.46 | -18.46 | 1.89 | 42.43 | 9.66 | 23.11 | 5.3 | 3.54 | -2.2 | 12.2 | -48.15 | 160 | 1460 | 13.4 | 0.15 | 14.99 | 20.76 | 60 | 9 | 9 | 0.36 | 96 | 99.2 | 285936.52 | 285936.52 | 20230204-163228_392e2257-671b-4dee-85c8-35d8b238f46b | 0
0 | 6 | 54.09 | 7.8 | [7.22, 0.92] | [21.47, 13.36] | [0.0, 0.0] | [15.14, 0.73] | 0 | 413.75 | 28.69 | 14.28 | 14.41 | 6.68 | 0 | 90 | 18.8 | 6 | 17.59 | -17.59 | 0.13 | 34.62 | 10.01 | 11.13 | 6.79 | 39.18 | -2.49 | 12.79 | -51.78 | 160 | 1460 | 13.4 | 0.15 | -15.42 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 423531.36 | 172101.2 | 20230204-163228_1d886f71-5eac-4070-a368-052da601ac6c | 14.351
0 | 6 | 57.83 | 7.8 | [0.17, 0.92] | [21.29, 13.36] | [0.0, 0.0] | [7.91, 0.73] | 0 | 46.63 | 21.46 | 14.28 | 7.18 | 6.31 | 0 | 85 | 20.1 | 6 | 18.25 | -18.25 | 1.24 | 37.01 | 9.05 | 17.91 | 5.34 | 29.3 | -2.33 | 12.47 | -48.99 | 160 | 1460 | 13.4 | 0.15 | 55.84 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 341582.63 | 172101.2 | 20230204-163228_5af75082-cda2-4678-a54d-ff0127ab1b83 | 9.6736
0 | 6 | 70.9 | 7.8 | [0.0, 0.92] | [18.17, 13.36] | [0.0, 0.0] | [4.62, 0.73] | 0 | 35 | 18.17 | 14.28 | 3.89 | 6.3 | 0 | 77 | 22.2 | 6 | 19.25 | -19.25 | 2.03 | 45.38 | 10.33 | 24.71 | 5.67 | 24.8 | -2.15 | 12.09 | -45.28 | 160 | 1460 | 13.4 | 0.15 | 13.07 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 269694.77 | 172101.2 | 20230204-163228_e4972e1b-d56c-4881-86fe-46218ff5ef74 | 5.5704
0 | 6 | 55.26 | 7.8 | [1.85, 0.92] | [21.52, 13.36] | [0.0, 0.0] | [9.83, 0.73] | 0 | 154.33 | 23.37 | 14.28 | 9.09 | 6.42 | 0 | 81 | 21.4 | 6 | 19 | -19 | 0.36 | 35.36 | 9.89 | 12.6 | 6.54 | 31.92 | -2.45 | 12.69 | -46.15 | 160 | 1460 | 13.4 | 0.15 | -20.88 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 365459.34 | 172101.2 | 20230204-163228_961034e0-fa5a-4d68-a862-515841e08b48 | 11.0364
0 | 6 | 80.17 | 7.8 | [0.0, 0.92] | [17.21, 13.36] | [0.0, 0.0] | [3.66, 0.73] | 0 | 35 | 17.21 | 14.28 | 2.93 | 6.3 | 0 | 91 | 20.2 | 6 | 19.09 | -19.09 | 2.29 | 51.31 | 11.68 | 27.95 | 6.41 | 23.5 | -2.04 | 11.89 | -45.83 | 160 | 1460 | 13.4 | 0.15 | 10.39 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 248340.85 | 172101.2 | 20230204-163228_8e8ac34c-987e-4707-bd39-e67a22fd5063 | 4.3516
0 | 6 | 76.53 | 7.8 | [0.0, 0.92] | [17.53, 13.36] | [0.0, 0.0] | [3.98, 0.73] | 0 | 35 | 17.53 | 14.28 | 3.25 | 6.3 | 0 | 95 | 18.9 | 6 | 18.29 | -18.29 | 2.19 | 48.98 | 11.15 | 26.67 | 6.12 | 23.94 | -2.08 | 11.97 | -48.81 | 160 | 1460 | 13.4 | 0.15 | 11.3 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 255484.49 | 172101.2 | 20230204-163228_b4cd858d-cbe2-462f-b0a3-1e74a4df1bca | 4.7593
0 | 6 | 54.69 | 7.8 | [3.45, 0.92] | [20.68, 13.36] | [0.0, 0.0] | [10.58, 0.73] | 0 | 250.05 | 24.13 | 14.28 | 9.85 | 6.51 | 0 | 90 | 19 | 6 | 17.78 | -17.78 | 0.22 | 35 | 9.99 | 11.73 | 6.71 | 32.95 | -2.47 | 12.75 | -50.91 | 160 | 1460 | 13.4 | 0.15 | -17.16 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 364207.55 | 172101.2 | 20230204-163228_6d69ac3d-5298-427f-9cd3-2d5b0d1ca158 | 10.965
0 | 6 | 66.38 | 7.8 | [0.0, 0.0] | [18.87, 18.87] | [0.0, 0.0] | [5.32, 5.32] | 0 | 35 | 18.87 | 18.87 | 0 | 6.3 | 0 | 94 | 18.6 | 6 | 17.87 | -17.87 | 1.9 | 42.48 | 9.67 | 23.14 | 5.31 | 3.54 | -2.2 | 12.2 | -50.53 | 160 | 1460 | 13.4 | 0.15 | 14.95 | 20.82 | 60 | 9 | 9 | 0.35 | 96 | 99.19 | 285565.12 | 285565.12 | 20230204-163228_6f48bf9a-3fb6-48df-8f49-6f2209e4b3af | 0
0 | 6 | 57.07 | 7.8 | [10.43, 0.92] | [24.9, 13.36] | [0.0, 0.0] | [21.78, 0.73] | 0 | 479.32 | 35.33 | 14.28 | 21.05 | 6.74 | 0 | 87 | 19.7 | 6 | 18.1 | -18.1 | 0.12 | 36.52 | 10.59 | 11.64 | 7.19 | 48.24 | -2.45 | 12.71 | -49.57 | 160 | 1460 | 13.4 | 0.15 | -15.21 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 535761.48 | 172101.2 | 20230204-163228_05325a78-0675-4039-8882-cffcc3b78bc6 | 20.7569
0 | 6 | 80.76 | 7.8 | [0.0, 0.92] | [17.17, 13.36] | [0.0, 0.0] | [3.62, 0.73] | 0 | 35 | 17.17 | 14.28 | 2.89 | 6.3 | 0 | 75 | 21.9 | 6 | 18.7 | -18.7 | 2.31 | 51.69 | 11.77 | 28.15 | 6.46 | 23.44 | -2.04 | 11.88 | -47.23 | 160 | 1460 | 13.4 | 0.15 | 10.25 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 247293.25 | 172101.2 | 20230204-163228_c57d0b80-8e56-42bc-8721-1c36d262d6ef | 4.2918
0 | 6 | 58.3 | 7.8 | [0.0, 0.0] | [21.22, 21.22] | [0.0, 0.0] | [7.67, 7.67] | 0 | 35 | 21.22 | 21.22 | 0 | 6.3 | 0 | 75 | 22.2 | 6 | 18.99 | -18.99 | 1.67 | 37.31 | 8.5 | 20.32 | 4.66 | 2.77 | -2.31 | 12.42 | -46.2 | 160 | 1460 | 13.4 | 0.15 | 20.13 | 14.46 | 60 | 9 | 9 | 0.51 | 96 | 100.6 | 338132.01 | 338132.01 | 20230204-163228_b5a51695-f7fc-43bc-b477-c4f3e78d5541 | 0
0 | 6 | 62.28 | 7.8 | [0.0, 0.92] | [19.79, 13.36] | [0.0, 0.0] | [6.24, 0.73] | 0 | 35 | 19.79 | 14.28 | 5.51 | 6.3 | 0 | 77 | 21.8 | 6 | 18.87 | -18.87 | 1.78 | 39.86 | 9.08 | 21.71 | 4.98 | 27.02 | -2.25 | 12.31 | -46.62 | 160 | 1460 | 13.4 | 0.15 | 17.2 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 306174.05 | 172101.2 | 20230204-163228_34a68c8f-5108-4dd4-9e08-83271423bc71 | 7.6526
0 | 6 | 68.43 | 7.8 | [0.0, 0.92] | [18.52, 13.36] | [0.0, 0.0] | [4.97, 0.73] | 0 | 35 | 18.52 | 14.28 | 4.24 | 6.3 | 0 | 72 | 22.2 | 6 | 18.59 | -18.59 | 1.96 | 43.8 | 9.97 | 23.85 | 5.47 | 25.29 | -2.18 | 12.15 | -47.64 | 160 | 1460 | 13.4 | 0.15 | 14.03 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 277713.8 | 172101.2 | 20230204-163228_cc6641b5-feb8-4e28-8b26-7e4531ffb807 | 6.0281
0 | 6 | 55.15 | 7.8 | [6.86, 0.92] | [24.92, 13.36] | [0.0, 0.0] | [18.24, 0.73] | 0 | 359.89 | 31.78 | 14.28 | 17.5 | 6.62 | 0 | 87 | 20 | 6 | 18.4 | -18.4 | 0.15 | 35.29 | 10.17 | 11.46 | 6.89 | 43.4 | -2.48 | 12.75 | -48.4 | 160 | 1460 | 13.4 | 0.15 | -15.83 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 497004.71 | 172101.2 | 20230204-163228_8e3e2b9d-9802-44f5-9363-e1daa40f923d | 18.5447
0 | 6 | 59.15 | 7.8 | [0.0, 0.92] | [20.84, 13.36] | [0.0, 0.0] | [7.29, 0.73] | 0 | 35 | 20.84 | 14.28 | 6.56 | 6.3 | 0 | 69 | 22.6 | 6 | 18.57 | -18.57 | 1.69 | 37.86 | 8.62 | 20.62 | 4.73 | 28.45 | -2.3 | 12.39 | -47.74 | 160 | 1460 | 13.4 | 0.15 | 19.42 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 329619.71 | 172101.2 | 20230204-163228_567ee266-6182-44d0-ba87-68d0b96308dd | 8.9908
0 | 6 | 69.02 | 7.8 | [0.0, 0.0] | [18.43, 18.43] | [0.0, 0.0] | [4.88, 4.88] | 0 | 35 | 18.43 | 18.43 | 0 | 6.3 | 0 | 94 | 18.7 | 6 | 17.97 | -17.97 | 1.97 | 44.18 | 10.06 | 24.06 | 5.52 | 3.77 | -2.17 | 12.14 | -50.11 | 160 | 1460 | 13.4 | 0.15 | 13.79 | 22.71 | 60 | 9 | 9 | 0.33 | 96 | 98.93 | 275664.44 | 275664.44 | 20230204-163228_ab778cfe-e213-44de-aaf0-af4f25431fe8 | 0
0 | 6 | 63.5 | 7.8 | [0.0, 0.0] | [19.48, 19.48] | [0.0, 0.0] | [5.93, 5.93] | 0 | 35 | 19.48 | 19.48 | 0 | 6.3 | 0 | 70 | 22.5 | 6 | 18.61 | -18.61 | 1.81 | 40.64 | 9.25 | 22.14 | 5.08 | 3.28 | -2.24 | 12.27 | -47.58 | 160 | 1460 | 13.4 | 0.15 | 16.46 | 18.7 | 60 | 9 | 9 | 0.4 | 96 | 99.56 | 299142.35 | 299142.35 | 20230204-163228_7d42abf7-549f-4481-94b0-d74d24357abe | 0
0 | 6 | 57.65 | 7.8 | [11.81, 0.92] | [24.44, 13.36] | [0.0, 0.0] | [22.7, 0.73] | 0 | 525.21 | 36.25 | 14.28 | 21.97 | 6.79 | 0 | 88 | 19.3 | 6 | 17.84 | -17.84 | 0.11 | 36.9 | 10.71 | 11.7 | 7.29 | 49.5 | -2.45 | 12.69 | -50.69 | 160 | 1460 | 13.4 | 0.15 | -15.06 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 540836.03 | 172101.2 | 20230204-163228_084d391c-0574-44fc-983f-3db91734c9a8 | 21.0465
0 | 6 | 55.87 | 7.8 | [0.0, 0.92] | [22.77, 13.36] | [0.0, 0.0] | [9.22, 0.73] | 0 | 35 | 22.77 | 14.28 | 8.49 | 6.3 | 0 | 82 | 20.7 | 6 | 18.45 | -18.45 | 1.6 | 35.75 | 8.14 | 19.47 | 4.47 | 31.09 | -2.34 | 12.49 | -48.18 | 160 | 1460 | 13.4 | 0.15 | 22.48 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 372931.02 | 172101.2 | 20230204-163228_232f0df2-d2fd-4d6a-9561-76ac96f8409f | 11.4629
0 | 6 | 62.02 | 7.8 | [0.75, 0.92] | [19.11, 13.36] | [0.0, 0.0] | [6.31, 0.73] | 0 | 91.84 | 19.86 | 14.28 | 5.58 | 6.36 | 0 | 91 | 19.3 | 6 | 18.2 | -18.2 | 0.68 | 39.69 | 10.69 | 15.63 | 6.87 | 27.12 | -2.32 | 12.45 | -49.17 | 160 | 1460 | 13.4 | 0.15 | -41.28 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 299233.78 | 172101.2 | 20230204-163228_ef90db46-46d1-4da8-8236-3e2a514ce119 | 7.2564
0 | 6 | 80.44 | 7.8 | [0.0, 0.92] | [17.19, 13.36] | [0.0, 0.0] | [3.64, 0.73] | 0 | 35 | 17.19 | 14.28 | 2.91 | 6.3 | 0 | 82 | 21.2 | 6 | 18.94 | -18.94 | 2.3 | 51.48 | 11.72 | 28.04 | 6.44 | 23.47 | -2.04 | 11.88 | -46.38 | 160 | 1460 | 13.4 | 0.15 | 10.32 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 247859.01 | 172101.2 | 20230204-163228_211f9cc0-c6b3-48d3-91a3-1ed4d03c7f63 | 4.3241
0 | 6 | 55.04 | 7.8 | [3.25, 0.92] | [20.39, 13.36] | [0.0, 0.0] | [10.09, 0.73] | 0 | 241.91 | 23.64 | 14.28 | 9.36 | 6.51 | 0 | 89 | 20.2 | 6 | 18.84 | -18.84 | 0.23 | 35.23 | 10.04 | 11.84 | 6.74 | 32.28 | -2.47 | 12.73 | -46.72 | 160 | 1460 | 13.4 | 0.15 | -17.35 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 355411.38 | 172101.2 | 20230204-163852_8ad59907-34b7-4839-9946-9cfea0696c68 | 10.4629
0 | 6 | 57.52 | 7.8 | [1.88, 0.92] | [19.74, 13.36] | [0.0, 0.0] | [8.07, 0.73] | 0 | 165.79 | 21.62 | 14.28 | 7.34 | 6.43 | 0 | 91 | 19.9 | 6 | 18.79 | -18.79 | 0.35 | 36.81 | 10.33 | 12.97 | 6.86 | 29.52 | -2.42 | 12.63 | -46.89 | 160 | 1460 | 13.4 | 0.15 | -20.52 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 325833.92 | 172101.2 | 20230204-163852_a0238ab2-eec5-4580-a9b7-395b2a5cf700 | 8.7747
0 | 6 | 55.5 | 7.8 | [1.79, 0.92] | [21.33, 13.36] | [0.0, 0.0] | [9.57, 0.73] | 0 | 151.76 | 23.12 | 14.28 | 8.84 | 6.42 | 0 | 69 | 21.8 | 6 | 17.83 | -17.83 | 0.37 | 35.52 | 9.92 | 12.69 | 6.56 | 31.57 | -2.44 | 12.69 | -50.74 | 160 | 1460 | 13.4 | 0.15 | -21.13 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 360375.44 | 172101.2 | 20230204-163852_9313205f-ffd4-482a-8e4b-90190fe206c2 | 10.7462
0 | 6 | 53.91 | 7.8 | [5.3, 0.92] | [21.37, 13.36] | [0.0, 0.0] | [13.13, 0.73] | 0 | 334.17 | 26.67 | 14.28 | 12.39 | 6.6 | 0 | 67 | 22.7 | 6 | 18.39 | -18.39 | 0.16 | 34.5 | 9.93 | 11.27 | 6.71 | 36.42 | -2.49 | 12.79 | -48.42 | 160 | 1460 | 13.4 | 0.15 | -15.98 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 400131.65 | 172101.2 | 20230204-163852_1304ddfc-af5f-4c90-81db-1d63ad22f719 | 13.0154
0 | 6 | 53.97 | 7.8 | [4.73, 0.92] | [21.4, 13.36] | [0.0, 0.0] | [12.57, 0.73] | 0 | 307.25 | 26.13 | 14.28 | 11.85 | 6.57 | 0 | 70 | 21.7 | 6 | 17.86 | -17.86 | 0.18 | 34.54 | 9.92 | 11.35 | 6.69 | 35.67 | -2.49 | 12.78 | -50.57 | 160 | 1460 | 13.4 | 0.15 | -16.26 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 394335.25 | 172101.2 | 20230204-163852_ad8b0826-c7db-4aa8-9ca0-ed0a3d544bb5 | 12.6846
0 | 6 | 54.08 | 7.8 | [4.43, 0.92] | [21.13, 13.36] | [0.0, 0.0] | [12.02, 0.73] | 0 | 295.88 | 25.56 | 14.28 | 11.28 | 6.56 | 0 | 71 | 21.7 | 6 | 17.99 | -17.99 | 0.18 | 34.61 | 9.93 | 11.41 | 6.7 | 34.91 | -2.49 | 12.77 | -50.02 | 160 | 1460 | 13.4 | 0.15 | -16.4 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 385158.76 | 172101.2 | 20230204-163852_84c1a374-b60c-4693-b453-c83eb51da72b | 12.1608
0 | 6 | 54 | 7.8 | [4.08, 0.92] | [21.83, 13.36] | [0.0, 0.0] | [12.36, 0.73] | 0 | 271.78 | 25.91 | 14.28 | 11.63 | 6.54 | 0 | 69 | 22 | 6 | 18.01 | -18.01 | 0.2 | 34.56 | 9.89 | 11.49 | 6.66 | 35.37 | -2.49 | 12.77 | -49.95 | 160 | 1460 | 13.4 | 0.15 | -16.73 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 396884.95 | 172101.2 | 20230204-163852_1fd1339f-62ab-4dcb-8781-3a8d1dbcf50a | 12.8301
0 | 6 | 61.55 | 7.8 | [0.0, 0.0] | [20.0, 20.0] | [0.0, 0.0] | [6.45, 6.45] | 0 | 35 | 20 | 20 | 0 | 6.3 | 0 | 75 | 21.7 | 6 | 18.52 | -18.52 | 1.76 | 39.39 | 8.97 | 21.45 | 4.92 | 3.1 | -2.26 | 12.33 | -47.94 | 160 | 1460 | 13.4 | 0.15 | 17.67 | 17.19 | 60 | 9 | 9 | 0.43 | 96 | 99.87 | 310846.66 | 310846.66 | 20230204-163852_78835765-2c43-408f-bd6e-32bdbc233ece | 0
0 | 6 | 58.21 | 7.8 | [1.56, 1.56] | [19.7, 19.7] | [0.0, 0.0] | [7.71, 7.71] | 0 | 145.27 | 21.26 | 21.26 | 0 | 6.41 | 0 | 71 | 21.6 | 6 | 17.9 | -17.9 | 0.4 | 37.25 | 10.38 | 13.4 | 6.85 | 2.76 | -2.4 | 12.6 | -50.42 | 160 | 1460 | 13.4 | 0.15 | -22.36 | 14.37 | 60 | 9 | 9 | 0.51 | 96 | 100.63 | 321406.12 | 321406.12 | 20230204-163852_57893447-e073-4651-a9f3-1eb7a23f4001 | 0
0 | 6 | 53.91 | 7.8 | [5.46, 0.92] | [21.95, 13.36] | [0.0, 0.0] | [13.86, 0.73] | 0 | 334.67 | 27.41 | 14.28 | 13.13 | 6.6 | 0 | 69 | 22.4 | 6 | 18.38 | -18.38 | 0.16 | 34.5 | 9.93 | 11.26 | 6.71 | 37.43 | -2.49 | 12.79 | -48.45 | 160 | 1460 | 13.4 | 0.15 | -15.98 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 414897.88 | 172101.2 | 20230204-163852_872877e1-d342-4fbe-9992-136e0723f9d9 | 13.8583
0 | 6 | 65.73 | 7.8 | [0.17, 0.17] | [18.83, 18.83] | [0.0, 0.0] | [5.45, 5.45] | 0 | 48.27 | 19 | 19 | 0 | 6.31 | 0 | 68 | 22 | 6 | 17.88 | -17.88 | 1.36 | 42.07 | 10.35 | 20.09 | 6.16 | 3.49 | -2.23 | 12.26 | -50.51 | 160 | 1460 | 13.4 | 0.15 | 37.06 | 20.35 | 60 | 9 | 9 | 0.36 | 96 | 99.27 | 286439.8 | 286439.8 | 20230204-163852_27fbb9ed-067a-4ce1-a42b-25e407e39ad5 | 0
0 | 6 | 58.39 | 7.8 | [0.28, 0.92] | [20.9, 13.36] | [0.0, 0.0] | [7.63, 0.73] | 0 | 54.72 | 21.18 | 14.28 | 6.9 | 6.32 | 0 | 67 | 22.3 | 6 | 18.02 | -18.02 | 1.07 | 37.37 | 9.41 | 17.07 | 5.72 | 28.91 | -2.34 | 12.48 | -49.9 | 160 | 1460 | 13.4 | 0.15 | 200.13 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 334037.77 | 172101.2 | 20230204-163852_e594e12f-a023-458f-933c-e78567b3faaf | 9.243
0 | 6 | 53.94 | 7.8 | [5.82, 0.92] | [21.89, 13.36] | [0.0, 0.0] | [14.16, 0.73] | 0 | 350.97 | 27.71 | 14.28 | 13.43 | 6.61 | 0 | 70 | 22.5 | 6 | 18.61 | -18.61 | 0.15 | 34.52 | 9.94 | 11.23 | 6.73 | 37.83 | -2.49 | 12.79 | -47.58 | 160 | 1460 | 13.4 | 0.15 | -15.84 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 417426.55 | 172101.2 | 20230204-163852_614230fe-fc29-4f43-b2ec-be9f90d430a5 | 14.0026
0 | 6 | 59.58 | 7.8 | [0.9, 0.92] | [19.77, 13.36] | [0.0, 0.0] | [7.12, 0.73] | 0 | 100.72 | 20.67 | 14.28 | 6.39 | 6.37 | 0 | 92 | 19.9 | 6 | 18.92 | -18.92 | 0.59 | 38.13 | 10.35 | 14.7 | 6.7 | 28.22 | -2.36 | 12.53 | -46.44 | 160 | 1460 | 13.4 | 0.15 | -32.81 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 315540.27 | 172101.2 | 20230204-163852_8ff3e106-9b4e-4f3c-a4e5-10f8fd65d6c8 | 8.1872
0 | 6 | 54.84 | 7.8 | [3.29, 0.92] | [20.61, 13.36] | [0.0, 0.0] | [10.35, 0.73] | 0 | 242.2 | 23.9 | 14.28 | 9.62 | 6.51 | 0 | 71 | 21.8 | 6 | 18.09 | -18.09 | 0.23 | 35.1 | 10.01 | 11.8 | 6.72 | 32.64 | -2.47 | 12.74 | -49.64 | 160 | 1460 | 13.4 | 0.15 | -17.33 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 360900.74 | 172101.2 | 20230204-163852_6b79eb15-c747-46dd-b538-1f564e6d7aab | 10.7762
0 | 6 | 53.91 | 7.8 | [4.84, 0.92] | [21.96, 13.36] | [0.0, 0.0] | [13.26, 0.73] | 0 | 306.97 | 26.8 | 14.28 | 12.52 | 6.57 | 0 | 68 | 22.1 | 6 | 17.97 | -17.97 | 0.18 | 34.5 | 9.9 | 11.34 | 6.69 | 36.6 | -2.49 | 12.78 | -50.12 | 160 | 1460 | 13.4 | 0.15 | -16.26 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 408345.28 | 172101.2 | 20230204-163852_b4201c25-4eac-4d7f-b1da-c17070788bbc | 13.4843
0 | 6 | 54.04 | 7.8 | [4.5, 0.92] | [21.22, 13.36] | [0.0, 0.0] | [12.17, 0.73] | 0 | 298.36 | 25.72 | 14.28 | 11.44 | 6.56 | 0 | 70 | 22.5 | 6 | 18.61 | -18.61 | 0.18 | 34.59 | 9.92 | 11.4 | 6.69 | 35.11 | -2.49 | 12.78 | -47.58 | 160 | 1460 | 13.4 | 0.15 | -16.37 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 387766.86 | 172101.2 | 20230204-163852_21dfcd71-d61f-4eac-9b8e-58136c6f9045 | 12.3097
0 | 6 | 65.27 | 7.8 | [0.0, 0.92] | [19.09, 13.36] | [0.0, 0.0] | [5.54, 0.73] | 0 | 35 | 19.09 | 14.28 | 4.81 | 6.3 | 0 | 80 | 21.1 | 6 | 18.59 | -18.59 | 1.86 | 41.77 | 9.51 | 22.75 | 5.22 | 26.06 | -2.21 | 12.23 | -47.67 | 160 | 1460 | 13.4 | 0.15 | 15.5 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 290407.37 | 172101.2 | 20230204-163852_683d379c-0c81-4f9b-8c14-b13444fa99b3 | 6.7526
0 | 6 | 54.12 | 7.8 | [3.41, 0.92] | [22.01, 13.36] | [0.0, 0.0] | [11.87, 0.73] | 0 | 236.64 | 25.42 | 14.28 | 11.14 | 6.5 | 0 | 74 | 21.9 | 6 | 18.57 | -18.57 | 0.23 | 34.64 | 9.87 | 11.67 | 6.62 | 34.71 | -2.48 | 12.76 | -47.72 | 160 | 1460 | 13.4 | 0.15 | -17.38 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 393576.98 | 172101.2 | 20230204-163852_93192c66-2e60-4b7d-9c3f-3cbb3931a92c | 12.6413
0 | 6 | 62.8 | 7.8 | [0.1, 0.92] | [19.55, 13.36] | [0.0, 0.0] | [6.1, 0.73] | 0 | 42.62 | 19.65 | 14.28 | 5.37 | 6.31 | 0 | 92 | 20 | 6 | 19.02 | -19.02 | 1.47 | 40.19 | 9.63 | 20.14 | 5.58 | 26.84 | -2.26 | 12.32 | -46.09 | 160 | 1460 | 13.4 | 0.15 | 28.3 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 301934.17 | 172101.2 | 20230204-163852_54809292-d8b5-488b-b6f3-8afb0c7150f5 | 7.4106
0 | 6 | 53.92 | 7.8 | [5.0, 0.92] | [21.49, 13.36] | [0.0, 0.0] | [12.95, 0.73] | 0 | 319.22 | 26.49 | 14.28 | 12.21 | 6.58 | 0 | 73 | 21.5 | 6 | 18.07 | -18.07 | 0.17 | 34.51 | 9.92 | 11.31 | 6.7 | 36.18 | -2.49 | 12.78 | -49.72 | 160 | 1460 | 13.4 | 0.15 | -16.13 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 399593.52 | 172101.2 | 20230204-163852_93e25903-9081-437c-909a-bb62432b2205 | 12.9847
0 | 6 | 54.42 | 7.8 | [3.07, 0.92] | [21.57, 13.36] | [0.0, 0.0] | [11.08, 0.73] | 0 | 222.35 | 24.64 | 14.28 | 10.36 | 6.49 | 0 | 68 | 22 | 6 | 17.88 | -17.88 | 0.24 | 34.83 | 9.9 | 11.82 | 6.63 | 33.63 | -2.47 | 12.75 | -50.51 | 160 | 1460 | 13.4 | 0.15 | -17.75 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 379807.99 | 172101.2 | 20230204-163852_9ab28186-2862-4a22-956c-3c4522b45ac2 | 11.8554
0 | 6 | 62.19 | 7.8 | [0.0, 0.92] | [19.82, 13.36] | [0.0, 0.0] | [6.27, 0.73] | 0 | 35 | 19.82 | 14.28 | 5.54 | 6.3 | 0 | 79 | 21.5 | 6 | 18.84 | -18.84 | 1.78 | 39.8 | 9.06 | 21.68 | 4.98 | 27.06 | -2.25 | 12.31 | -46.73 | 160 | 1460 | 13.4 | 0.15 | 17.25 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 306708.42 | 172101.2 | 20230204-163852_be190a79-6a95-47c8-b05f-e74f9439b3bc | 7.6831
0 | 6 | 53.92 | 7.8 | [4.81, 0.92] | [21.74, 13.36] | [0.0, 0.0] | [13.0, 0.73] | 0 | 307.53 | 26.55 | 14.28 | 12.27 | 6.57 | 0 | 73 | 21.8 | 6 | 18.35 | -18.35 | 0.18 | 34.51 | 9.91 | 11.34 | 6.69 | 36.25 | -2.49 | 12.78 | -48.59 | 160 | 1460 | 13.4 | 0.15 | -16.25 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 402959.59 | 172101.2 | 20230204-163852_71345143-f3b8-45fa-a817-ff2dc27eaef5 | 13.1768
0 | 6 | 62.01 | 7.8 | [0.0, 0.92] | [19.87, 13.36] | [0.0, 0.0] | [6.32, 0.73] | 0 | 35 | 19.87 | 14.28 | 5.59 | 6.3 | 0 | 76 | 21.8 | 6 | 18.74 | -18.74 | 1.77 | 39.69 | 9.04 | 21.62 | 4.96 | 27.13 | -2.26 | 12.31 | -47.1 | 160 | 1460 | 13.4 | 0.15 | 17.37 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 307836.48 | 172101.2 | 20230204-163852_2c7361aa-55cf-4672-8dbb-35bfdde4aaa8 | 7.7474
0 | 6 | 64.58 | 7.8 | [0.0, 0.92] | [19.23, 13.36] | [0.0, 0.0] | [5.68, 0.73] | 0 | 35 | 19.23 | 14.28 | 4.95 | 6.3 | 0 | 84 | 21.2 | 6 | 19.19 | -19.19 | 1.85 | 41.33 | 9.41 | 22.51 | 5.17 | 26.26 | -2.22 | 12.25 | -45.49 | 160 | 1460 | 13.4 | 0.15 | 15.86 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 293634.12 | 172101.2 | 20230204-163852_29dfe2b2-e8b3-40a5-bdb4-8bdca9b16afb | 6.9368
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 583.14 | 7.8 | [0.0, 0.92] | [13.88, 13.36] | [0.0, 0.0] | [0.33, 0.73] | 0 | 35 | 13.88 | 14.28 | -0.4 | 6.3 | 0 | 64 | 22.1 | 6 | 17.44 | -17.44 | 16.66 | 373.21 | 84.97 | 203.27 | 46.65 | 18.95 | -0.41 | 8.61 | -52.46 | 160 | 1460 | 13.4 | 0.15 | 0.86 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 173488.58 | 172101.2 | 20230204-164514_65e59cc7-a64c-4e45-b834-7fef7b1ebdfa | 0.079188
0 | 6 | 83.71 | 7.8 | [0.0, 0.92] | [16.95, 13.36] | [0.0, 0.0] | [3.4, 0.73] | 0 | 35 | 16.95 | 14.28 | 2.67 | 6.3 | 0 | 70 | 22.2 | 6 | 18.33 | -18.33 | 2.39 | 53.57 | 12.2 | 29.18 | 6.7 | 23.15 | -2.01 | 11.82 | -48.66 | 160 | 1460 | 13.4 | 0.15 | 9.63 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 242487.05 | 172101.2 | 20230204-164514_839e933d-fbbc-4c9f-a003-fc9a71d216bb | 4.0175
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 164.99 | 7.8 | [0.0, 0.92] | [14.88, 13.36] | [0.0, 0.0] | [1.33, 0.73] | 0 | 35 | 14.88 | 14.28 | 0.6 | 6.3 | 0 | 75 | 21.6 | 6 | 18.42 | -18.42 | 4.71 | 105.6 | 24.04 | 57.51 | 13.2 | 20.31 | -1.45 | 10.7 | -48.31 | 160 | 1460 | 13.4 | 0.15 | 3.61 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 195949.53 | 172101.2 | 20230204-164514_1bb62aef-2a50-423f-abf6-443f25699192 | 1.3612
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 103.52 | 7.8 | [0.0, 0.92] | [16.0, 13.36] | [0.0, 0.0] | [2.45, 0.73] | 0 | 35 | 16 | 14.28 | 1.72 | 6.3 | 0 | 73 | 22.1 | 6 | 18.63 | -18.63 | 2.96 | 66.25 | 15.08 | 36.08 | 8.28 | 21.85 | -1.83 | 11.47 | -47.5 | 160 | 1460 | 13.4 | 0.15 | 6.85 | 151.4 | 60 | 9 | 9 | 0.05 | 96 | 96.44 | 221105.89 | 172101.2 | 20230204-164514_25da6688-3873-4b27-bcba-db7d4f61ebb0 | 2.7971
0 | 6 | 72.48 | 7.8 | [0.0, 0.0] | [17.97, 17.97] | [0.0, 0.0] | [4.42, 4.42] | 0 | 35 | 17.97 | 17.97 | 0 | 6.3 | 0 | 68 | 22.1 | 6 | 17.97 | -17.97 | 2.07 | 46.38 | 10.56 | 25.26 | 5.8 | 4.07 | -2.13 | 12.06 | -50.12 | 160 | 1460 | 13.4 | 0.15 | 12.52 | 25.1 | 60 | 9 | 9 | 0.29 | 96 | 98.65 | 265230.67 | 265230.67 | 20230204-164514_4fe29a84-02e9-4731-8a3f-8b8a9cd627a9 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## A2
supply_temp | return_temp | ct_conductivity | ct_ph | Bore | CWRO | BoilerBD | BD | scheme | mu_conductivity | mu_flow(PV) | mu-flow(OV) | m-saving(PV-OV) | mu_ph | cooling_tower_level | relative_humidity | ambient_temp | delta_temp | wetBulb_temp | approach_temp | cond_coc | ct_tds | ct_ca | ct_alk | ct_chloride | flow_cycle | sat_index | sta_index | perf_index | system_vol | rec_rate | evap_loss | drift_loss | blowdown_coc | hold_time_index | dosing_residual | dosing_contact_time | dosing_density | dosing_continuous | dosing_initial | dosing_slug | currentOperatingCost | newOperatingCost | updatedDateTime | 3806.7027
0 | 8.1 | 1500.64 | 7.8 | [41.84, 38.87] | [10.0, 11.36] | [0.0, 0.0] | [9.34, 7.73] | 0 | 2307.46 | 51.84 | 50.23 | 1.61 | 7.44 | 0 | 44 | 22.5 | 8.1 | 14.96 | -14.96 | 0.65 | 960.41 | 251.42 | 161.26 | 195.55 | 6.71 | -0.08 | 7.96 | -118 | 980 | 8765 | 108.62 | 0.88 | -310.66 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 254228.84 | 251909.9 | 20230204-160652_2002ecfe-bd5b-4d66-b73c-bc6b1d75d014 | 0.13236
0 | 8.1 | 1621.25 | 7.8 | [41.03, 41.03] | [10.0, 10.0] | [0.0, 0.0] | [8.53, 8.53] | 0 | 2312.75 | 51.03 | 51.03 | 0 | 7.44 | 0 | 46 | 21.7 | 8.1 | 14.59 | -14.59 | 0.7 | 1037.6 | 271.48 | 173.56 | 211.28 | 5.98 | -0.02 | 7.83 | -124.82 | 980 | 8765 | 108.62 | 0.88 | -363.3 | 79.63 | 60 | 9 | 9 | 0.57 | 588 | 593.12 | 245250.97 | 245250.97 | 20230204-160652_99555fc7-8c3b-4882-a6f7-4504d0b92880 | 0
0 | 8.1 | 753.22 | 7.8 | [45.74, 42.81] | [20.0, 8.19] | [0.0, 0.0] | [23.24, 8.5] | 0 | 2113.74 | 65.74 | 51 | 14.74 | 7.37 | 0 | 63 | 19.9 | 8.1 | 15.3 | -15.3 | 0.36 | 482.06 | 126.5 | 82.59 | 98.08 | 7.73 | -0.64 | 9.07 | -112.45 | 980 | 8765 | 108.62 | 0.88 | -168.76 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 521484.79 | 224283.22 | 20230204-160652_112b7c4b-48f6-4fee-9835-c897f50db736 | 16.9636
0 | 8.1 | 1365.81 | 7.8 | [42.96, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [10.46, 8.5] | 0 | 2300.31 | 52.96 | 51 | 1.96 | 7.45 | 0 | 87 | 17.2 | 8.1 | 15.66 | -15.66 | 0.59 | 874.12 | 229 | 147.52 | 177.96 | 6.23 | -0.15 | 8.11 | -107.14 | 980 | 8765 | 108.62 | 0.88 | -267.38 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 266556.08 | 224283.22 | 20230204-160652_e00046a6-6eb4-4c3d-a232-5e88faccf455 | 2.4128
0 | 8.1 | 724.91 | 7.8 | [46.17, 42.81] | [21.0, 8.19] | [0.0, 0.0] | [24.67, 8.5] | 0 | 2096.39 | 67.17 | 51 | 16.17 | 7.36 | 0 | 63 | 19.6 | 8.1 | 15.03 | -15.03 | 0.35 | 463.94 | 121.78 | 79.66 | 94.38 | 7.9 | -0.67 | 9.13 | -116.88 | 980 | 8765 | 108.62 | 0.88 | -166.04 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 548694.64 | 224283.22 | 20230204-160652_fab0dbb8-028f-4138-acb0-0f679b3742bd | 18.5166
0 | 8.1 | 651.73 | 7.8 | [47.93, 47.64] | [24.0, 4.31] | [0.0, 0.0] | [29.43, 9.44] | 0 | 2044.84 | 71.93 | 51.95 | 19.98 | 7.34 | 0 | 68 | 17.8 | 8.1 | 13.99 | -13.99 | 0.32 | 417.11 | 109.6 | 72.21 | 84.83 | 7.62 | -0.75 | 9.3 | -137.46 | 980 | 8765 | 108.62 | 0.88 | -159.44 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 635371.46 | 190517.28 | 20230204-160652_6eb5ef77-735c-4259-917e-f1e351772977 | 25.3912
0 | 8.1 | 784.96 | 7.8 | [44.33, 42.81] | [20.0, 8.19] | [0.0, 0.0] | [21.82, 8.5] | 0 | 2119.91 | 64.33 | 51 | 13.33 | 7.36 | 0 | 56 | 20.9 | 8.1 | 15.29 | -15.29 | 0.37 | 502.38 | 131.71 | 85.54 | 102.22 | 7.57 | -0.61 | 9.01 | -112.7 | 980 | 8765 | 108.62 | 0.88 | -172.5 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 505879.39 | 224283.22 | 20230204-160652_d3ca2bbe-cc61-4fde-8bfc-9ffe281ed7a3 | 16.0728
0 | 8.1 | 1305.56 | 7.8 | [43.55, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [11.05, 8.5] | 0 | 2296.58 | 53.55 | 51 | 2.55 | 7.45 | 0 | 50 | 21.9 | 8.1 | 15.33 | -15.33 | 0.57 | 835.56 | 218.98 | 141.39 | 170.1 | 6.3 | -0.19 | 8.18 | -111.99 | 980 | 8765 | 108.62 | 0.88 | -251.72 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 273081.84 | 224283.22 | 20230204-160652_270e0bcf-5337-4ce8-af48-c8601e639e04 | 2.7853
0 | 8.1 | 1575.14 | 7.8 | [41.32, 41.32] | [10.0, 10.0] | [0.0, 0.0] | [8.82, 8.82] | 0 | 2310.83 | 51.32 | 51.32 | 0 | 7.44 | 0 | 49 | 20.8 | 8.1 | 14.25 | -14.25 | 0.68 | 1008.09 | 263.81 | 168.85 | 205.26 | 5.82 | -0.04 | 7.88 | -131.72 | 980 | 8765 | 108.62 | 0.88 | -341.19 | 76.98 | 60 | 9 | 9 | 0.59 | 588 | 593.29 | 248491.06 | 248491.06 | 20230204-160652_39b8955b-2c79-4917-ac03-a0880fdbbd46 | 0
0 | 8.1 | 1600.6 | 7.8 | [41.16, 41.16] | [10.0, 10.0] | [0.0, 0.0] | [8.66, 8.66] | 0 | 2311.9 | 51.16 | 51.16 | 0 | 7.44 | 0 | 47 | 22.2 | 8.1 | 15.16 | -15.16 | 0.69 | 1024.38 | 268.04 | 171.45 | 208.58 | 5.91 | -0.03 | 7.85 | -114.78 | 980 | 8765 | 108.62 | 0.88 | -353.05 | 78.44 | 60 | 9 | 9 | 0.58 | 588 | 593.19 | 246674.93 | 246674.93 | 20230204-160652_c45e770a-13ee-47de-8283-022dba0e284a | 0
0 | 8.1 | 700.19 | 7.8 | [47.59, 47.64] | [21.0, 4.31] | [0.0, 0.0] | [26.09, 9.44] | 0 | 2090.59 | 68.59 | 51.95 | 16.64 | 7.37 | 0 | 65 | 18.4 | 8.1 | 14.18 | -14.18 | 0.33 | 448.12 | 117.73 | 77.41 | 91.16 | 7.26 | -0.69 | 9.19 | -133.15 | 980 | 8765 | 108.62 | 0.88 | -163.33 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 564299.6 | 190517.28 | 20230204-160652_d36adc95-942a-49a8-bced-44922c013e5e | 21.3346
0 | 8.1 | 751.71 | 7.8 | [45.81, 42.81] | [20.0, 8.19] | [0.0, 0.0] | [23.31, 8.5] | 0 | 2113.43 | 65.81 | 51 | 14.81 | 7.37 | 0 | 62 | 20.3 | 8.1 | 15.54 | -15.54 | 0.36 | 481.09 | 126.25 | 82.46 | 97.88 | 7.74 | -0.64 | 9.08 | -108.9 | 980 | 8765 | 108.62 | 0.88 | -168.59 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 522277.73 | 224283.22 | 20230204-160652_0e42a183-e08c-4610-b39f-fa7f74843969 | 17.0088
0 | 8.1 | 1307.16 | 7.8 | [42.53, 42.81] | [11.0, 8.19] | [0.0, 0.0] | [11.03, 8.5] | 0 | 2284.2 | 53.53 | 51 | 2.53 | 7.44 | 0 | 84 | 18.4 | 8.1 | 16.47 | -16.47 | 0.57 | 836.58 | 219.1 | 140.95 | 170.32 | 6.3 | -0.19 | 8.18 | -96.74 | 980 | 8765 | 108.62 | 0.88 | -253.95 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 284286.28 | 224283.22 | 20230204-160652_c3b98b40-ab60-425a-bdda-7e718e56c562 | 3.4248
0 | 8.1 | 731.98 | 7.8 | [46.8, 42.81] | [20.0, 8.19] | [0.0, 0.0] | [24.3, 8.5] | 0 | 2109.2 | 66.8 | 51 | 15.8 | 7.37 | 0 | 64 | 18.8 | 8.1 | 14.43 | -14.43 | 0.35 | 468.47 | 123.01 | 80.63 | 95.3 | 7.86 | -0.66 | 9.12 | -128.03 | 980 | 8765 | 108.62 | 0.88 | -166.36 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 533167.1 | 224283.22 | 20230204-160652_5abd403a-d726-45f8-b7e4-b4cdbe6cc1a9 | 17.6304
0 | 8.1 | 858 | 7.8 | [42.66, 42.81] | [19.0, 8.19] | [0.0, 0.0] | [19.16, 8.5] | 0 | 2143.61 | 61.66 | 51 | 10.66 | 7.37 | 0 | 53 | 21.4 | 8.1 | 15.32 | -15.32 | 0.4 | 549.12 | 143.81 | 92.78 | 111.75 | 7.25 | -0.54 | 8.87 | -112.2 | 980 | 8765 | 108.62 | 0.88 | -181.12 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 465114.71 | 224283.22 | 20230204-160652_4eff511c-025f-4e1b-9331-9f4deb00d65a | 13.7461
0 | 8.1 | 1400.35 | 7.8 | [41.65, 38.87] | [11.0, 11.36] | [0.0, 0.0] | [10.15, 7.73] | 0 | 2289.71 | 52.65 | 50.23 | 2.42 | 7.43 | 0 | 69 | 18.6 | 8.1 | 14.85 | -14.85 | 0.61 | 896.22 | 234.58 | 150.39 | 182.47 | 6.81 | -0.14 | 8.07 | -119.92 | 980 | 8765 | 108.62 | 0.88 | -279.66 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 274511.27 | 251909.9 | 20230204-160652_4527b027-783a-4a3e-800c-f2dc34ec0830 | 1.29
0 | 8.1 | 1510.69 | 7.8 | [41.77, 38.87] | [10.0, 11.36] | [0.0, 0.0] | [9.27, 7.73] | 0 | 2307.93 | 51.77 | 50.23 | 1.54 | 7.44 | 0 | 44 | 22.6 | 8.1 | 15.05 | -15.05 | 0.65 | 966.84 | 253.09 | 162.28 | 196.86 | 6.7 | -0.07 | 7.95 | -116.59 | 980 | 8765 | 108.62 | 0.88 | -314.46 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 253415.81 | 251909.9 | 20230204-160652_c5c6454b-51a1-4fda-aa0d-529316b48465 | 0.085954
0 | 8.1 | 1507.9 | 7.8 | [41.79, 38.87] | [10.0, 11.36] | [0.0, 0.0] | [9.29, 7.73] | 0 | 2307.8 | 51.79 | 50.23 | 1.56 | 7.44 | 0 | 48 | 21 | 8.1 | 14.28 | -14.28 | 0.65 | 965.06 | 252.63 | 162 | 196.49 | 6.7 | -0.07 | 7.95 | -131.04 | 980 | 8765 | 108.62 | 0.88 | -313.39 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 253639.99 | 251909.9 | 20230204-160652_43d4023c-0c77-4e81-b9d5-c8c178f24cb5 | 0.098749
0 | 8.1 | 1388.74 | 7.8 | [41.75, 42.81] | [11.0, 8.19] | [0.0, 0.0] | [10.25, 8.5] | 0 | 2289.07 | 52.75 | 51 | 1.75 | 7.43 | 0 | 66 | 18.5 | 8.1 | 14.4 | -14.4 | 0.61 | 888.79 | 232.65 | 149.21 | 180.96 | 6.21 | -0.14 | 8.08 | -128.63 | 980 | 8765 | 108.62 | 0.88 | -276.17 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 275642.41 | 224283.22 | 20230204-160652_74f0b3d5-caf9-4b5d-9a08-558e397f3fc9 | 2.9315
0 | 8.1 | 1475.88 | 7.8 | [42.03, 38.87] | [10.0, 11.36] | [0.0, 0.0] | [9.53, 7.73] | 0 | 2306.25 | 52.03 | 50.23 | 1.8 | 7.44 | 0 | 45 | 22.2 | 8.1 | 14.86 | -14.86 | 0.64 | 944.57 | 247.3 | 158.73 | 192.32 | 6.73 | -0.09 | 7.98 | -119.77 | 980 | 8765 | 108.62 | 0.88 | -301.69 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 256289.67 | 251909.9 | 20230204-160652_326510b5-793c-4963-82db-7429b7c8d3f9 | 0.24999
0 | 8.1 | 687.16 | 7.8 | [47.4, 42.81] | [22.0, 8.19] | [0.0, 0.0] | [26.9, 8.5] | 0 | 2076.26 | 69.4 | 51 | 18.4 | 7.36 | 0 | 66 | 18.1 | 8.1 | 14.03 | -14.03 | 0.33 | 439.78 | 115.52 | 75.93 | 89.46 | 8.16 | -0.71 | 9.22 | -136.61 | 980 | 8765 | 108.62 | 0.88 | -162.36 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 584705.76 | 224283.22 | 20230204-160652_93b80a35-d03b-42cf-8cf3-91bfa591a408 | 20.5721
0 | 8.1 | 1761.43 | 7.8 | [40.25, 40.25] | [10.0, 10.0] | [0.0, 0.0] | [7.75, 7.75] | 0 | 2317.91 | 50.25 | 50.25 | 0 | 7.44 | 0 | 44 | 22.9 | 8.1 | 15.3 | -15.3 | 0.76 | 1127.32 | 294.79 | 187.87 | 229.56 | 6.49 | 0.05 | 7.7 | -112.54 | 980 | 8765 | 108.62 | 0.88 | -452.46 | 87.68 | 60 | 9 | 9 | 0.52 | 588 | 592.65 | 236608.75 | 236608.75 | 20230204-160652_a2aa0c9a-f8b5-486a-af18-6b7e3297075c | 0
0 | 8.1 | 1191.31 | 7.8 | [43.88, 42.81] | [11.0, 8.19] | [0.0, 0.0] | [12.38, 8.5] | 0 | 2275.98 | 54.88 | 51 | 3.88 | 7.44 | 0 | 86 | 17.1 | 8.1 | 15.45 | -15.45 | 0.52 | 762.44 | 199.86 | 129.25 | 155.21 | 6.46 | -0.26 | 8.33 | -110.27 | 980 | 8765 | 108.62 | 0.88 | -227.93 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 299142.12 | 224283.22 | 20230204-160652_f8fc4306-d166-453b-8e33-a2ee021bbac5 | 4.2728
0 | 8.1 | 1525.45 | 7.8 | [41.66, 38.87] | [10.0, 11.36] | [0.0, 0.0] | [9.16, 7.73] | 0 | 2308.62 | 51.66 | 50.23 | 1.43 | 7.44 | 0 | 46 | 22.2 | 8.1 | 15.01 | -15.01 | 0.66 | 976.29 | 255.54 | 163.79 | 198.78 | 6.69 | -0.06 | 7.93 | -117.21 | 980 | 8765 | 108.62 | 0.88 | -320.2 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 252244.28 | 251909.9 | 20230204-160652_7992da71-1662-43de-ae95-8d1b6fd30c32 | 0.019086
0 | 8.1 | 707.99 | 7.8 | [43.12, 42.81] | [25.0, 8.19] | [0.0, 0.0] | [25.62, 8.5] | 0 | 2047.93 | 68.12 | 51 | 17.12 | 7.32 | 0 | 68 | 17.8 | 8.1 | 13.99 | -13.99 | 0.35 | 453.11 | 118.69 | 76.85 | 92.18 | 8.01 | -0.69 | 9.19 | -137.46 | 980 | 8765 | 108.62 | 0.88 | -166.02 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 604729.71 | 224283.22 | 20230204-160652_a922fd44-3964-4aa1-8c28-94ef9c927970 | 21.715
0 | 8.1 | 743.44 | 7.8 | [46.21, 42.81] | [20.0, 8.19] | [0.0, 0.0] | [23.71, 8.5] | 0 | 2111.69 | 66.21 | 51 | 15.21 | 7.37 | 0 | 63 | 19.3 | 8.1 | 14.76 | -14.76 | 0.35 | 475.8 | 124.89 | 81.69 | 96.8 | 7.79 | -0.65 | 9.09 | -121.66 | 980 | 8765 | 108.62 | 0.88 | -167.65 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 526727.76 | 224283.22 | 20230204-160652_21b5fbc6-6c83-4713-9b12-4d34ca9034c0 | 17.2628
0 | 8.1 | 1140.97 | 7.8 | [44.58, 42.81] | [11.0, 8.19] | [0.0, 0.0] | [13.07, 8.5] | 0 | 2271.81 | 55.58 | 51 | 4.58 | 7.44 | 0 | 86 | 16.8 | 8.1 | 15.15 | -15.15 | 0.5 | 730.22 | 191.5 | 124.17 | 148.64 | 6.54 | -0.3 | 8.4 | -114.85 | 980 | 8765 | 108.62 | 0.88 | -218.22 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 306806.19 | 224283.22 | 20230204-161315_91352dc8-45fd-49f7-87fc-1fac06cdd8b8 | 4.7102
0 | 8.1 | 1794.84 | 7.8 | [20.08, 20.07] | [30.0, 26.48] | [0.0, 0.0] | [7.58, 4.05] | 0 | 2061.92 | 50.08 | 46.55 | 3.53 | 7.18 | 0 | 70 | 22.6 | 8.1 | 18.7 | -18.7 | 0.87 | 1148.7 | 295.58 | 172.02 | 234.05 | 12.37 | 0.01 | 7.77 | -76.4 | 980 | 8765 | 108.62 | 0.88 | -838.61 | 167.78 | 60 | 9 | 9 | 0.27 | 588 | 590.43 | 462539.27 | 383465.53 | 20230204-161315_c18632b4-4ec0-4111-9546-4b496a50f4e3 | 4.5133
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1298.94 | 7.8 | [18.62, 19.13] | [35.0, 27.24] | [0.0, 0.0] | [11.12, 3.86] | 0 | 1984.22 | 53.62 | 46.37 | 7.25 | 7.14 | 0 | 81 | 17.8 | 8.1 | 15.54 | -15.54 | 0.65 | 831.32 | 213.62 | 123.51 | 169.36 | 13.88 | -0.26 | 8.32 | -108.94 | 980 | 8765 | 108.62 | 0.88 | -314.52 | 175.77 | 60 | 9 | 9 | 0.26 | 588 | 590.32 | 558543.98 | 390043.31 | 20230204-161315_337ac0c4-cca7-4eb2-ae61-2531d62b51af | 9.6176
0 | 8.1 | 1221.37 | 7.8 | [16.5, 16.09] | [38.0, 29.68] | [0.0, 0.0] | [12.0, 3.27] | 0 | 1943.84 | 54.5 | 45.77 | 8.73 | 7.11 | 0 | 76 | 19.9 | 8.1 | 16.94 | -16.94 | 0.63 | 781.67 | 200.46 | 114.56 | 159.25 | 16.67 | -0.32 | 8.43 | -91.67 | 980 | 8765 | 108.62 | 0.88 | -292.26 | 207.73 | 60 | 9 | 9 | 0.22 | 588 | 589.96 | 602422.28 | 411294.6 | 20230204-161315_020ccc41-143d-4620-b7f7-e36c202f57e7 | 10.9091
0 | 8.1 | 1181.96 | 7.8 | [45.0, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [12.5, 8.5] | 0 | 2287.58 | 55 | 51 | 4 | 7.45 | 0 | 82 | 16.7 | 8.1 | 14.59 | -14.59 | 0.52 | 756.45 | 198.44 | 128.84 | 153.98 | 6.47 | -0.27 | 8.34 | -124.76 | 980 | 8765 | 108.62 | 0.88 | -224.75 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 289114.94 | 224283.22 | 20230204-161315_c9d3decf-a54e-412b-8ef8-74b7809bf909 | 3.7004
0 | 8.1 | 1252.96 | 7.8 | [44.13, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [11.62, 8.5] | 0 | 2293 | 54.13 | 51 | 3.13 | 7.45 | 0 | 78 | 16.9 | 8.1 | 14.32 | -14.32 | 0.55 | 801.89 | 210.24 | 136.05 | 163.24 | 6.37 | -0.22 | 8.24 | -130.2 | 980 | 8765 | 108.62 | 0.88 | -239.49 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 279419.96 | 224283.22 | 20230204-161315_c0f709e6-9c3e-497a-add1-63f302d9413a | 3.1471
0 | 8.1 | 1293.95 | 7.8 | [19.67, 22.25] | [34.0, 24.73] | [0.0, 0.0] | [11.17, 4.47] | 0 | 1996.5 | 53.67 | 46.98 | 6.69 | 7.15 | 0 | 78 | 21.6 | 8.1 | 18.81 | -18.81 | 0.65 | 828.13 | 213 | 123.87 | 168.7 | 12 | -0.26 | 8.32 | -75.64 | 980 | 8765 | 108.62 | 0.88 | -308.69 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 547736.89 | 368232.77 | 20230204-161315_44539f67-e12a-4365-a761-45da7ef788f4 | 10.2457
0 | 8.1 | 7776.12 | 7.8 | [23.08, 47.64] | [21.0, 4.31] | [0.0, 0.0] | [1.57, 9.44] | 0 | 2212.09 | 44.08 | 51.95 | -7.87 | 7.27 | 0 | 73 | 19.3 | 8.1 | 16 | -16 | 3.52 | 4976.72 | 1284.15 | 757.4 | 1014.27 | 4.67 | 1.23 | 5.34 | -102.56 | 980 | 8765 | 108.62 | 0.88 | 43.19 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 293753.23 | 190517.28 | 20230204-161315_abeba2c6-e346-4579-9497-9f57a5a2e960 | 5.8925
0 | 8.1 | 1226.7 | 7.8 | [43.44, 42.81] | [11.0, 8.19] | [0.0, 0.0] | [11.93, 8.5] | 0 | 2278.68 | 54.44 | 51 | 3.44 | 7.44 | 0 | 87 | 17 | 8.1 | 15.46 | -15.46 | 0.54 | 785.09 | 205.74 | 132.82 | 159.82 | 6.4 | -0.24 | 8.28 | -109.99 | 980 | 8765 | 108.62 | 0.88 | -235.29 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 294228.29 | 224283.22 | 20230204-161315_41eeefb3-8790-454e-93c1-b3a04ffe9dd2 | 3.9923
0 | 8.1 | 1232.76 | 7.8 | [22.36, 22.25] | [32.0, 24.73] | [0.0, 0.0] | [11.86, 4.47] | 0 | 2018.71 | 54.36 | 46.98 | 7.38 | 7.18 | 0 | 84 | 16.5 | 8.1 | 14.63 | -14.63 | 0.61 | 788.96 | 203.42 | 120.01 | 160.71 | 12.15 | -0.29 | 8.38 | -124.05 | 980 | 8765 | 108.62 | 0.88 | -279 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 532571.54 | 368232.77 | 20230204-161315_90fcb8fb-987a-45e6-86ab-f76005e7639b | 9.3801
0 | 8.1 | 2494.24 | 7.8 | [22.74, 22.25] | [25.0, 24.73] | [0.0, 0.0] | [5.24, 4.47] | 0 | 2138.16 | 47.74 | 46.98 | 0.76 | 7.23 | 0 | 86 | 16 | 8.1 | 14.37 | -14.37 | 1.17 | 1596.31 | 411.75 | 242.78 | 325.27 | 10.67 | 0.29 | 7.22 | -129.14 | 980 | 8765 | 108.62 | 0.88 | 652.27 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 379744.46 | 368232.77 | 20230204-161315_17c1cd67-cae8-437a-9652-d5c19437b078 | 0.65706
0 | 8.1 | 1539.81 | 7.8 | [17.56, 18.27] | [34.0, 27.93] | [0.0, 0.0] | [9.06, 3.7] | 0 | 2004.63 | 51.56 | 46.2 | 5.36 | 7.14 | 0 | 74 | 21.5 | 8.1 | 18.2 | -18.2 | 0.77 | 985.48 | 252.99 | 145.29 | 200.8 | 13.95 | -0.12 | 8.04 | -80.22 | 980 | 8765 | 108.62 | 0.88 | -468.47 | 183.76 | 60 | 9 | 9 | 0.25 | 588 | 590.22 | 524442.04 | 396049.11 | 20230204-161315_8eee0256-59bc-4ce3-a30a-5382b8e20255 | 7.3284
0 | 8.1 | 1455.74 | 7.8 | [18.19, 18.27] | [34.0, 27.93] | [0.0, 0.0] | [9.69, 3.7] | 0 | 2002.19 | 52.19 | 46.2 | 5.99 | 7.14 | 0 | 77 | 21.4 | 8.1 | 18.49 | -18.49 | 0.73 | 931.67 | 239.31 | 137.95 | 189.82 | 14.12 | -0.17 | 8.13 | -77.97 | 980 | 8765 | 108.62 | 0.88 | -398 | 183.76 | 60 | 9 | 9 | 0.25 | 588 | 590.22 | 531340.54 | 396049.11 | 20230204-161315_5e25c133-a876-4251-b978-b5a07e0a77bd | 7.7221
0 | 8.1 | 1142.14 | 7.8 | [45.56, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [13.06, 8.5] | 0 | 2284.2 | 55.56 | 51 | 4.56 | 7.45 | 0 | 86 | 16.5 | 8.1 | 14.86 | -14.86 | 0.5 | 730.97 | 191.82 | 124.8 | 148.79 | 6.54 | -0.29 | 8.39 | -119.82 | 980 | 8765 | 108.62 | 0.88 | -217.26 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 295231.21 | 224283.22 | 20230204-161315_9307c778-4377-450c-bcb6-c822eb934dd8 | 4.0495
0 | 8.1 | 1855.22 | 7.8 | [19.8, 21.1] | [30.0, 25.65] | [0.0, 0.0] | [7.3, 4.25] | 0 | 2063.18 | 49.8 | 46.75 | 3.05 | 7.18 | 0 | 63 | 23.1 | 8.1 | 18.21 | -18.21 | 0.9 | 1187.34 | 305.45 | 177.47 | 241.93 | 11.72 | 0.04 | 7.72 | -80.1 | 980 | 8765 | 108.62 | 0.88 | -1077.68 | 159.79 | 60 | 9 | 9 | 0.28 | 588 | 590.55 | 459425.01 | 376229.97 | 20230204-161315_74a80635-e644-4046-9984-5c01f8576e73 | 4.7486
0 | 8.1 | 1234.82 | 7.8 | [43.34, 42.81] | [11.0, 8.19] | [0.0, 0.0] | [11.84, 8.5] | 0 | 2279.28 | 54.34 | 51 | 3.34 | 7.44 | 0 | 86 | 17.3 | 8.1 | 15.64 | -15.64 | 0.54 | 790.28 | 207.09 | 133.64 | 160.88 | 6.39 | -0.24 | 8.27 | -107.42 | 980 | 8765 | 108.62 | 0.88 | -237.05 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 293151.46 | 224283.22 | 20230204-161315_e1290cce-948e-4477-b98c-ec25375053c9 | 3.9308
0 | 8.1 | 1399.5 | 7.8 | [42.66, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [10.16, 8.5] | 0 | 2302.24 | 52.66 | 51 | 1.66 | 7.45 | 0 | 77 | 17 | 8.1 | 14.3 | -14.3 | 0.61 | 895.68 | 234.6 | 150.95 | 182.35 | 6.19 | -0.13 | 8.07 | -130.64 | 980 | 8765 | 108.62 | 0.88 | -277.02 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 263205.83 | 224283.22 | 20230204-161315_20fbdb18-33e5-4e31-bfe1-76df41a7e202 | 2.2216
0 | 8.1 | 1422.6 | 7.8 | [22.46, 22.25] | [30.0, 24.73] | [0.0, 0.0] | [9.96, 4.47] | 0 | 2051.54 | 52.46 | 46.98 | 5.48 | 7.19 | 0 | 86 | 16 | 8.1 | 14.37 | -14.37 | 0.69 | 910.47 | 234.77 | 138.48 | 185.47 | 11.73 | -0.17 | 8.14 | -129.14 | 980 | 8765 | 108.62 | 0.88 | -354.33 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 488778.84 | 368232.77 | 20230204-161315_d2524044-50c0-471e-9160-5ca0a60c9f8e | 6.8805
0 | 8.1 | 2222.87 | 7.8 | [19.45, 24.93] | [29.0, 22.57] | [0.0, 0.0] | [5.95, 5.0] | 0 | 2082.32 | 48.45 | 47.5 | 0.95 | 7.19 | 0 | 61 | 23 | 8.1 | 17.84 | -17.84 | 1.07 | 1422.64 | 365.87 | 212.06 | 289.9 | 9.69 | 0.19 | 7.43 | -83.12 | 980 | 8765 | 108.62 | 0.88 | 1609.39 | 135.82 | 60 | 9 | 9 | 0.33 | 588 | 591 | 433166.16 | 349415.84 | 20230204-161315_6230373d-14ce-422d-8422-db746e92b142 | 4.7803
0 | 8.1 | 1230.13 | 7.8 | [20.39, 20.07] | [34.0, 26.48] | [0.0, 0.0] | [11.89, 4.05] | 0 | 1993.79 | 54.39 | 46.55 | 7.84 | 7.15 | 0 | 84 | 16.8 | 8.1 | 14.92 | -14.92 | 0.62 | 787.29 | 202.63 | 118.32 | 160.37 | 13.44 | -0.3 | 8.39 | -118.76 | 980 | 8765 | 108.62 | 0.88 | -283.6 | 167.78 | 60 | 9 | 9 | 0.27 | 588 | 590.43 | 555694.89 | 383465.53 | 20230204-161315_0ef14bcd-df90-453b-922f-49d6953fa13e | 9.8304
0 | 8.1 | 1167.78 | 7.8 | [16.2, 16.76] | [39.0, 29.14] | [0.0, 0.0] | [12.69, 3.4] | 0 | 1929.23 | 55.2 | 45.9 | 9.3 | 7.1 | 0 | 73 | 21.2 | 8.1 | 17.79 | -17.79 | 0.61 | 747.38 | 191.6 | 109.34 | 152.26 | 16.23 | -0.35 | 8.51 | -83.63 | 980 | 8765 | 108.62 | 0.88 | -275.21 | 199.74 | 60 | 9 | 9 | 0.23 | 588 | 590.04 | 621483.29 | 406619.31 | 20230204-161315_db37e0d8-9ac0-4cc2-b48e-c9dca0847f67 | 12.2639
0 | 8.1 | 1228.48 | 7.8 | [45.41, 42.81] | [9.0, 8.19] | [0.0, 0.0] | [11.91, 8.5] | 0 | 2303.6 | 54.41 | 51 | 3.41 | 7.46 | 0 | 86 | 16.4 | 8.1 | 14.76 | -14.76 | 0.53 | 786.23 | 206.31 | 134.12 | 160.05 | 6.4 | -0.24 | 8.27 | -121.58 | 980 | 8765 | 108.62 | 0.88 | -232.74 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 271214.76 | 224283.22 | 20230204-161315_07de088f-9dd3-4dda-97cf-d19eb18679a3 | 2.6787
0 | 8.1 | 1147.55 | 7.8 | [45.48, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [12.98, 8.5] | 0 | 2284.67 | 55.48 | 51 | 4.48 | 7.45 | 0 | 85 | 16.7 | 8.1 | 14.94 | -14.94 | 0.5 | 734.43 | 192.72 | 125.35 | 149.5 | 6.53 | -0.29 | 8.38 | -118.43 | 980 | 8765 | 108.62 | 0.88 | -218.25 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 294367.63 | 224283.22 | 20230204-161315_47794b0e-b598-4ecd-8308-11c4a9b03d20 | 4.0003
0 | 8.1 | 13502.83 | 7.8 | [23.4, 47.64] | [20.0, 4.31] | [0.0, 0.0] | [0.9, 9.44] | 0 | 2229.85 | 43.4 | 51.95 | -8.55 | 7.28 | 0 | 79 | 17.1 | 8.1 | 14.63 | -14.63 | 6.06 | 8641.81 | 2230.51 | 1317.39 | 1761.27 | 4.59 | 1.69 | 4.43 | -124.07 | 980 | 8765 | 108.62 | 0.88 | 21.49 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 274874.24 | 190517.28 | 20230204-161315_d9e3c717-33a5-4af7-99f2-d8211b14a626 | 4.8149
0 | 8.1 | 1307.38 | 7.8 | [17.53, 20.07] | [36.0, 26.48] | [0.0, 0.0] | [11.03, 4.05] | 0 | 1972.06 | 53.53 | 46.55 | 6.98 | 7.12 | 0 | 78 | 18.9 | 8.1 | 16.23 | -16.23 | 0.66 | 836.72 | 214.79 | 123.43 | 170.47 | 13.23 | -0.26 | 8.31 | -99.63 | 980 | 8765 | 108.62 | 0.88 | -322.28 | 167.78 | 60 | 9 | 9 | 0.27 | 588 | 590.43 | 568961.56 | 383465.53 | 20230204-161315_4fac19bf-be0e-4830-b177-06b8b932ab9b | 10.5877
0 | 8.1 | 1134.22 | 7.8 | [22.67, 22.25] | [33.0, 24.73] | [0.0, 0.0] | [13.17, 4.47] | 0 | 2001.32 | 55.67 | 46.98 | 8.69 | 7.17 | 0 | 63 | 22.9 | 8.1 | 18.03 | -18.03 | 0.57 | 725.9 | 187.2 | 110.68 | 147.85 | 12.44 | -0.36 | 8.51 | -81.57 | 980 | 8765 | 108.62 | 0.88 | -250.71 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 558438.22 | 368232.77 | 20230204-161940_b5aa3c25-f98c-4548-a6bd-aefc752f69df | 10.8565
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 501.54 | 7.8 | [52.73, 47.64] | [41.0, 4.31] | [0.0, 0.0] | [51.23, 9.44] | 0 | 1817.19 | 93.73 | 51.95 | 41.78 | 7.25 | 0 | 89 | 19.9 | 8.1 | 18.55 | -18.55 | 0.28 | 320.99 | 84.57 | 56.9 | 65.21 | 9.92 | -0.96 | 9.71 | -77.53 | 980 | 8765 | 108.62 | 0.88 | -150.03 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1069578.42 | 190517.28 | 20230204-161940_669a4f16-6e26-47c3-bd3d-f0b3d1d0b95e | 50.1747
0 | 8.1 | 969.95 | 7.8 | [17.67, 17.48] | [41.0, 28.56] | [0.0, 0.0] | [16.17, 3.54] | 0 | 1894.52 | 58.67 | 46.04 | 12.63 | 7.09 | 0 | 83 | 20.8 | 8.1 | 18.68 | -18.68 | 0.51 | 620.77 | 159.36 | 91.84 | 126.43 | 16.57 | -0.5 | 8.8 | -76.59 | 980 | 8765 | 108.62 | 0.88 | -222.58 | 191.75 | 60 | 9 | 9 | 0.24 | 588 | 590.13 | 682600.6 | 401554.42 | 20230204-161940_1696e315-f61f-4157-9758-68c416da3ba7 | 16.0414
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 541.15 | 7.8 | [43.89, 42.81] | [41.0, 8.19] | [0.0, 0.0] | [42.38, 8.5] | 0 | 1833.33 | 84.89 | 51 | 33.89 | 7.21 | 0 | 84 | 20.7 | 8.1 | 18.71 | -18.71 | 0.3 | 346.33 | 90.74 | 59.2 | 70.4 | 9.99 | -0.91 | 9.62 | -76.38 | 980 | 8765 | 108.62 | 0.88 | -154.11 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 971960.34 | 224283.22 | 20230204-161940_a2738943-0b03-446e-b973-af40f204db84 | 42.6756
0 | 8.1 | 1282.6 | 7.8 | [13.8, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [11.29, 9.44] | 0 | 1921.29 | 53.8 | 51.95 | 1.85 | 7.08 | 0 | 97 | 17.7 | 8.1 | 17.34 | -17.34 | 0.67 | 820.87 | 209.96 | 118.05 | 167.26 | 5.7 | -0.28 | 8.37 | -87.7 | 980 | 8765 | 108.62 | 0.88 | -326.77 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 617408.17 | 190517.28 | 20230204-161940_f5f80809-4d1f-4fc5-b958-c04a0e03ef20 | 24.3659
0 | 8.1 | 713.38 | 7.8 | [27.81, 28.34] | [40.0, 19.83] | [0.0, 0.0] | [25.31, 5.67] | 0 | 1881.64 | 67.81 | 48.17 | 19.64 | 7.15 | 0 | 77 | 21.2 | 8.1 | 18.3 | -18.3 | 0.38 | 456.56 | 118.23 | 71.98 | 92.92 | 11.97 | -0.72 | 9.25 | -79.43 | 980 | 8765 | 108.62 | 0.88 | -174.95 | 119.85 | 60 | 9 | 9 | 0.38 | 588 | 591.4 | 772118.9 | 325581.05 | 20230204-161940_71363234-a300-4312-9579-39e8b34096b7 | 25.4873
0 | 8.1 | 1559.28 | 7.8 | [21.43, 22.25] | [30.0, 24.73] | [0.0, 0.0] | [8.93, 4.47] | 0 | 2055.98 | 51.43 | 46.98 | 4.45 | 7.19 | 0 | 61 | 23 | 8.1 | 17.84 | -17.84 | 0.76 | 997.94 | 257.1 | 150.78 | 203.31 | 11.5 | -0.1 | 8 | -83.12 | 980 | 8765 | 108.62 | 0.88 | -449.63 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 477418.17 | 368232.77 | 20230204-161940_55fd6eec-b5c6-42ff-94f0-3f6212519031 | 6.232
0 | 8.1 | 824.44 | 7.8 | [23.8, 23.51] | [39.0, 23.71] | [0.0, 0.0] | [20.3, 4.72] | 0 | 1906.43 | 62.8 | 47.22 | 15.58 | 7.14 | 0 | 66 | 22.6 | 8.1 | 18.16 | -18.16 | 0.43 | 527.64 | 136.19 | 81.2 | 107.42 | 13.3 | -0.62 | 9.03 | -80.48 | 980 | 8765 | 108.62 | 0.88 | -191.39 | 143.81 | 60 | 9 | 9 | 0.31 | 588 | 590.83 | 705393.78 | 359347 | 20230204-161940_7f7d2fa2-4db7-4bfc-a70a-bf94d004b1c4 | 19.7515
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1812 | 7.8 | [20.0, 20.07] | [30.0, 26.48] | [0.0, 0.0] | [7.5, 4.05] | 0 | 2062.29 | 50 | 46.55 | 3.45 | 7.18 | 0 | 62 | 23.3 | 8.1 | 18.25 | -18.25 | 0.88 | 1159.68 | 298.39 | 173.57 | 236.29 | 12.35 | 0.02 | 7.76 | -79.77 | 980 | 8765 | 108.62 | 0.88 | -895.03 | 167.78 | 60 | 9 | 9 | 0.27 | 588 | 590.43 | 461629.99 | 383465.53 | 20230204-161940_4e8d8934-b950-42ab-91de-02eab0731f3f | 4.4614
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 512.25 | 7.8 | [50.91, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [48.41, 9.44] | 0 | 1831.67 | 90.91 | 51.95 | 38.96 | 7.25 | 0 | 92 | 19.1 | 8.1 | 18.13 | -18.13 | 0.28 | 327.84 | 86.28 | 57.69 | 66.61 | 9.63 | -0.94 | 9.68 | -80.78 | 980 | 8765 | 108.62 | 0.88 | -150.8 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1027057.76 | 190517.28 | 20230204-161940_b098edc8-b0f1-4c75-a2af-7f67c5b1a006 | 47.7477
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 517.81 | 7.8 | [49.59, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [47.09, 9.44] | 0 | 1834.13 | 89.59 | 51.95 | 37.64 | 7.24 | 0 | 95 | 18.6 | 8.1 | 17.99 | -17.99 | 0.28 | 331.4 | 87.15 | 58.01 | 67.34 | 9.49 | -0.94 | 9.67 | -81.86 | 980 | 8765 | 108.62 | 0.88 | -151.36 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1012496.52 | 190517.28 | 20230204-161940_24999d64-ae9a-4bf1-9e01-545f40a200af | 46.9166
0 | 8.1 | 947 | 7.8 | [19.2, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [16.7, 9.44] | 0 | 1904.95 | 59.2 | 51.95 | 7.25 | 7.11 | 0 | 90 | 19.4 | 8.1 | 18.18 | -18.18 | 0.5 | 606.08 | 155.81 | 90.58 | 123.43 | 6.27 | -0.52 | 8.83 | -80.37 | 980 | 8765 | 108.62 | 0.88 | -216.01 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 677097.52 | 190517.28 | 20230204-161940_55dd3712-5842-40af-bdac-f0237564dada | 27.7728
0 | 8.1 | 627.29 | 7.8 | [34.0, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [31.49, 9.44] | 0 | 1866.66 | 74 | 51.95 | 22.05 | 7.18 | 0 | 96 | 18.1 | 8.1 | 17.62 | -17.62 | 0.34 | 401.47 | 104.46 | 65.46 | 81.67 | 7.83 | -0.81 | 9.43 | -85.12 | 980 | 8765 | 108.62 | 0.88 | -163.6 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 840371.55 | 190517.28 | 20230204-161940_7f6e81ff-6745-494e-aae9-8fb1819f0153 | 37.0921
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1460.31 | 7.8 | [22.15, 22.25] | [30.0, 24.73] | [0.0, 0.0] | [9.65, 4.47] | 0 | 2052.85 | 52.15 | 46.98 | 5.17 | 7.19 | 0 | 62 | 22.9 | 8.1 | 17.89 | -17.89 | 0.71 | 934.6 | 240.93 | 141.87 | 190.39 | 11.66 | -0.15 | 8.1 | -82.72 | 980 | 8765 | 108.62 | 0.88 | -376.32 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 485389.31 | 368232.77 | 20230204-161940_16b7d7f2-6364-44cd-b718-af28e797449f | 6.687
0 | 8.1 | 669.49 | 7.8 | [30.6, 30.41] | [40.0, 18.17] | [0.0, 0.0] | [28.1, 6.07] | 0 | 1874.71 | 70.6 | 48.58 | 22.02 | 7.16 | 0 | 90 | 19.8 | 8.1 | 18.57 | -18.57 | 0.36 | 428.48 | 111.2 | 68.61 | 87.18 | 11.63 | -0.77 | 9.34 | -77.34 | 980 | 8765 | 108.62 | 0.88 | -168.96 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 802928.04 | 311109.93 | 20230204-161940_011fb6e1-ac91-412d-8071-8965b7627169 | 28.0718
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 521.2 | 7.8 | [40.83, 38.87] | [48.0, 11.36] | [0.0, 0.0] | [46.33, 7.73] | 0 | 1758.3 | 88.83 | 50.23 | 38.6 | 7.16 | 0 | 86 | 21 | 8.1 | 19.25 | -19.25 | 0.3 | 333.57 | 87.21 | 56.35 | 67.8 | 11.5 | -0.95 | 9.7 | -72.65 | 980 | 8765 | 108.62 | 0.88 | -154.39 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 1095196.16 | 251909.9 | 20230204-162602_f75dbaf7-3d38-45a0-93cd-f27506314615 | 48.1328
0 | 8.1 | 767.02 | 7.8 | [27.1, 26.53] | [38.0, 21.28] | [0.0, 0.0] | [22.6, 5.31] | 0 | 1911.44 | 65.1 | 47.81 | 17.29 | 7.16 | 0 | 84 | 21.3 | 8.1 | 19.29 | -19.29 | 0.4 | 490.89 | 127.05 | 77.02 | 99.92 | 12.25 | -0.67 | 9.13 | -72.4 | 980 | 8765 | 108.62 | 0.88 | -181.43 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 719432.77 | 338243.28 | 20230204-162602_db6e0a5f-c355-4cd8-8129-4f8633a2f92e | 21.7574
0 | 8.1 | 532.69 | 7.8 | [56.46, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [43.96, 9.44] | 0 | 1938.21 | 86.46 | 51.95 | 34.51 | 7.33 | 0 | 98 | 16.7 | 8.1 | 16.45 | -16.45 | 0.27 | 340.92 | 90.03 | 61.12 | 69.28 | 9.15 | -0.9 | 9.6 | -96.98 | 980 | 8765 | 108.62 | 0.88 | -149.79 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 864031.3 | 190517.28 | 20230204-162602_a0537208-1951-4fe6-b9d7-d3f77f3698b1 | 38.4426
0 | 8.1 | 541.96 | 7.8 | [54.74, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [42.24, 9.44] | 0 | 1942.71 | 84.74 | 51.95 | 32.79 | 7.32 | 0 | 98 | 17.1 | 8.1 | 16.85 | -16.85 | 0.28 | 346.85 | 91.51 | 61.79 | 70.49 | 8.97 | -0.89 | 9.58 | -92.53 | 980 | 8765 | 108.62 | 0.88 | -150.65 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 845100.61 | 190517.28 | 20230204-162602_1ad30b17-4fbc-4f3e-a995-e7e0ad0ce9a1 | 37.3621
0 | 8.1 | 554.42 | 7.8 | [51.67, 47.64] | [31.0, 4.31] | [0.0, 0.0] | [40.17, 9.44] | 0 | 1938.23 | 82.67 | 51.95 | 30.72 | 7.31 | 0 | 97 | 16.8 | 8.1 | 16.44 | -16.44 | 0.29 | 354.83 | 93.44 | 62.48 | 72.12 | 8.75 | -0.88 | 9.55 | -97.18 | 980 | 8765 | 108.62 | 0.88 | -152.14 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 833613.51 | 190517.28 | 20230204-162602_35725284-e655-4bdd-9c7f-64255cac374b | 36.7064
0 | 8.1 | 746.58 | 7.8 | [27.06, 26.53] | [39.0, 21.28] | [0.0, 0.0] | [23.56, 5.31] | 0 | 1897.45 | 66.06 | 47.81 | 18.25 | 7.15 | 0 | 85 | 21 | 8.1 | 19.12 | -19.12 | 0.39 | 477.81 | 123.66 | 74.98 | 97.25 | 12.43 | -0.69 | 9.18 | -73.48 | 980 | 8765 | 108.62 | 0.88 | -179.09 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 741391.47 | 338243.28 | 20230204-162602_6402f738-41ad-49a3-925b-08f6a2748f4a | 23.0107
0 | 8.1 | 535.26 | 7.8 | [55.96, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [43.46, 9.44] | 0 | 1939.49 | 85.96 | 51.95 | 34.01 | 7.33 | 0 | 98 | 16.8 | 8.1 | 16.55 | -16.55 | 0.28 | 342.56 | 90.44 | 61.3 | 69.62 | 9.1 | -0.9 | 9.59 | -95.83 | 980 | 8765 | 108.62 | 0.88 | -150.03 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 858602.68 | 190517.28 | 20230204-162602_8f298c37-cf64-402d-94f8-78d928747063 | 38.1327
0 | 8.1 | 667.83 | 7.8 | [41.72, 42.81] | [29.0, 8.19] | [0.0, 0.0] | [28.22, 8.5] | 0 | 1994.63 | 70.72 | 51 | 19.72 | 7.29 | 0 | 97 | 16.9 | 8.1 | 16.54 | -16.54 | 0.33 | 427.41 | 111.85 | 72.11 | 86.94 | 8.32 | -0.74 | 9.29 | -96.02 | 980 | 8765 | 108.62 | 0.88 | -163.3 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 678967.22 | 224283.22 | 20230204-162602_6ee43f9d-1c3f-490d-a050-08ec37dfcaeb | 25.9523
0 | 8.1 | 749.07 | 7.8 | [26.94, 26.53] | [39.0, 21.28] | [0.0, 0.0] | [23.44, 5.31] | 0 | 1897.78 | 65.94 | 47.81 | 18.13 | 7.15 | 0 | 85 | 21 | 8.1 | 19.12 | -19.12 | 0.39 | 479.4 | 124.06 | 75.17 | 97.58 | 12.41 | -0.69 | 9.17 | -73.48 | 980 | 8765 | 108.62 | 0.88 | -179.46 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 740055.26 | 338243.28 | 20230204-162602_90ef631e-a868-43ff-9ee3-a9d271025600 | 22.9345
0 | 8.1 | 497.45 | 7.8 | [45.92, 47.64] | [49.0, 4.31] | [0.0, 0.0] | [52.42, 9.44] | 0 | 1740.79 | 94.92 | 51.95 | 42.97 | 7.18 | 0 | 80 | 22 | 8.1 | 19.45 | -19.45 | 0.29 | 318.37 | 83.51 | 55.02 | 64.68 | 10.05 | -0.98 | 9.75 | -71.37 | 980 | 8765 | 108.62 | 0.88 | -152.08 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1173858.33 | 190517.28 | 20230204-162602_99045306-03a0-4762-9b7c-0c8277dbc925 | 56.1268
0 | 8.1 | 736.24 | 7.8 | [27.58, 28.34] | [39.0, 19.83] | [0.0, 0.0] | [24.08, 5.67] | 0 | 1896.07 | 66.58 | 48.17 | 18.41 | 7.16 | 0 | 90 | 19.7 | 8.1 | 18.47 | -18.47 | 0.39 | 471.19 | 122 | 74.16 | 95.9 | 11.75 | -0.7 | 9.2 | -78.08 | 980 | 8765 | 108.62 | 0.88 | -177.58 | 119.85 | 60 | 9 | 9 | 0.38 | 588 | 591.4 | 747105.09 | 325581.05 | 20230204-162602_f6a6d0fb-a0f1-4555-93d1-4688dd52685a | 24.0596
0 | 8.1 | 785.21 | 7.8 | [26.31, 28.34] | [38.0, 19.83] | [0.0, 0.0] | [21.81, 5.67] | 0 | 1913.66 | 64.31 | 48.17 | 16.14 | 7.16 | 0 | 85 | 20.5 | 8.1 | 18.64 | -18.64 | 0.41 | 502.54 | 129.99 | 78.49 | 102.3 | 11.35 | -0.65 | 9.1 | -76.88 | 980 | 8765 | 108.62 | 0.88 | -184.21 | 119.85 | 60 | 9 | 9 | 0.38 | 588 | 591.4 | 710747.06 | 325581.05 | 20230204-162602_55c4c123-e1f6-47b3-9608-d1900a8c47f8 | 21.9844
0 | 8.1 | 534.37 | 7.8 | [56.13, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [43.63, 9.44] | 0 | 1939.05 | 86.13 | 51.95 | 34.18 | 7.33 | 0 | 96 | 17.1 | 8.1 | 16.62 | -16.62 | 0.28 | 342 | 90.3 | 61.24 | 69.5 | 9.12 | -0.9 | 9.6 | -95.1 | 980 | 8765 | 108.62 | 0.88 | -149.95 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 860449.93 | 190517.28 | 20230204-162602_8be5066a-76cd-4808-9a0c-89cdb3de2d8a | 38.2382
0 | 8.1 | 496.76 | 7.8 | [46.13, 42.81] | [49.0, 8.19] | [0.0, 0.0] | [52.63, 8.5] | 0 | 1740.53 | 95.13 | 51 | 44.13 | 7.18 | 0 | 79 | 22 | 8.1 | 19.32 | -19.32 | 0.29 | 317.92 | 83.41 | 54.99 | 64.59 | 11.19 | -0.98 | 9.75 | -72.19 | 980 | 8765 | 108.62 | 0.88 | -152.01 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 1176158.35 | 224283.22 | 20230204-162602_68e631f7-fe63-4606-be36-47dc9a792f90 | 54.3308
0 | 8.1 | 665.02 | 7.8 | [30.92, 30.41] | [40.0, 18.17] | [0.0, 0.0] | [28.42, 6.07] | 0 | 1873.93 | 70.92 | 48.58 | 22.34 | 7.17 | 0 | 89 | 20.4 | 8.1 | 19.04 | -19.04 | 0.35 | 425.61 | 110.49 | 68.28 | 86.6 | 11.68 | -0.77 | 9.35 | -74.05 | 980 | 8765 | 108.62 | 0.88 | -168.38 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 806479.28 | 311109.93 | 20230204-162602_432aac77-3e85-4667-84ed-4536c19bc1a3 | 28.2745
0 | 8.1 | 538.08 | 7.8 | [56.44, 47.64] | [29.0, 4.31] | [0.0, 0.0] | [42.94, 9.44] | 0 | 1950.74 | 85.44 | 51.95 | 33.49 | 7.33 | 0 | 97 | 17.1 | 8.1 | 16.74 | -16.74 | 0.28 | 344.37 | 90.94 | 61.72 | 69.99 | 9.05 | -0.89 | 9.58 | -93.8 | 980 | 8765 | 108.62 | 0.88 | -150 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 841408.13 | 190517.28 | 20230204-162602_df9e1869-b550-4c2b-8981-f7679fbcbf21 | 37.1513
0 | 8.1 | 737.45 | 7.8 | [32.52, 32.79] | [34.0, 16.25] | [0.0, 0.0] | [24.01, 6.54] | 0 | 1952.59 | 66.52 | 49.04 | 17.48 | 7.21 | 0 | 95 | 18.7 | 8.1 | 18.09 | -18.09 | 0.38 | 471.97 | 122.68 | 76.21 | 96.05 | 10.17 | -0.68 | 9.17 | -81.05 | 980 | 8765 | 108.62 | 0.88 | -174.55 | 103.87 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 689481.75 | 294412.49 | 20230204-162602_ebe99646-f5e2-422b-98da-f07c1bd2b4c9 | 22.5496
0 | 8.1 | 664.75 | 7.8 | [40.94, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [28.44, 8.5] | 0 | 1982.98 | 70.94 | 51 | 19.94 | 7.28 | 0 | 97 | 18.1 | 8.1 | 17.74 | -17.74 | 0.34 | 425.44 | 111.27 | 71.54 | 86.54 | 8.35 | -0.75 | 9.3 | -84.06 | 980 | 8765 | 108.62 | 0.88 | -163.4 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 692819.14 | 224283.22 | 20230204-162602_f7f0ce25-407c-4b30-968e-a967772b3d1d | 26.7429
0 | 8.1 | 540.53 | 7.8 | [56.0, 47.64] | [29.0, 4.31] | [0.0, 0.0] | [42.49, 9.44] | 0 | 1951.94 | 85 | 51.95 | 33.05 | 7.33 | 0 | 98 | 16.6 | 8.1 | 16.35 | -16.35 | 0.28 | 345.94 | 91.33 | 61.9 | 70.31 | 9 | -0.89 | 9.58 | -98.16 | 980 | 8765 | 108.62 | 0.88 | -150.22 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 836518.14 | 190517.28 | 20230204-162602_59b604ee-f80e-429e-9f33-a8d2fe874ab9 | 36.8722
0 | 8.1 | 497.18 | 7.8 | [46.0, 42.81] | [49.0, 8.19] | [0.0, 0.0] | [52.5, 8.5] | 0 | 1740.69 | 95 | 51 | 44 | 7.18 | 0 | 80 | 22 | 8.1 | 19.45 | -19.45 | 0.29 | 318.19 | 83.47 | 55.01 | 64.65 | 11.18 | -0.98 | 9.75 | -71.37 | 980 | 8765 | 108.62 | 0.88 | -152.05 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 1174757.35 | 224283.22 | 20230204-162602_80f6217c-e0f0-4c1a-b291-b25f8547d817 | 54.2508
0 | 8.1 | 538.37 | 7.8 | [55.39, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [42.88, 9.44] | 0 | 1941 | 85.39 | 51.95 | 33.44 | 7.32 | 0 | 98 | 17.1 | 8.1 | 16.85 | -16.85 | 0.28 | 344.56 | 90.94 | 61.53 | 70.02 | 9.04 | -0.89 | 9.59 | -92.53 | 980 | 8765 | 108.62 | 0.88 | -150.32 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 852213.9 | 190517.28 | 20230204-162602_b4176341-9e94-4677-8a3b-64dc122428ec | 37.7681
0 | 8.1 | 654.2 | 7.8 | [41.74, 38.87] | [30.0, 11.36] | [0.0, 0.0] | [29.24, 7.73] | 0 | 1980.45 | 71.74 | 50.23 | 21.51 | 7.28 | 0 | 97 | 17.3 | 8.1 | 16.94 | -16.94 | 0.33 | 418.69 | 109.56 | 70.67 | 85.16 | 9.28 | -0.76 | 9.32 | -91.67 | 980 | 8765 | 108.62 | 0.88 | -162.21 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 701570.75 | 251909.9 | 20230204-162602_99be4bf4-0735-420d-b4ff-792e3783208c | 25.6656
0 | 8.1 | 497.34 | 7.8 | [45.95, 42.81] | [49.0, 8.19] | [0.0, 0.0] | [52.45, 8.5] | 0 | 1740.75 | 94.95 | 51 | 43.95 | 7.18 | 0 | 78 | 22 | 8.1 | 19.19 | -19.19 | 0.29 | 318.3 | 83.5 | 55.02 | 64.67 | 11.17 | -0.98 | 9.75 | -73.04 | 980 | 8765 | 108.62 | 0.88 | -152.07 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 1174203.7 | 224283.22 | 20230204-162602_1682a359-b710-4c8c-b165-638bbb24d498 | 54.2192
0 | 8.1 | 1008.93 | 7.8 | [27.84, 26.53] | [30.0, 21.28] | [0.0, 0.0] | [15.34, 5.31] | 0 | 2029.49 | 57.84 | 47.81 | 10.03 | 7.22 | 0 | 98 | 17 | 8.1 | 16.75 | -16.75 | 0.5 | 645.71 | 167.25 | 101.47 | 131.48 | 10.89 | -0.44 | 8.68 | -93.61 | 980 | 8765 | 108.62 | 0.88 | -216.01 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 548172.39 | 338243.28 | 20230204-162602_8e4c90e8-c938-4dbc-85f2-1b8b57d6a6ed | 11.9823
0 | 8.1 | 497.42 | 7.8 | [44.93, 42.81] | [50.0, 8.19] | [0.0, 0.0] | [52.43, 8.5] | 0 | 1731.48 | 94.93 | 51 | 43.93 | 7.17 | 0 | 85 | 20.8 | 8.1 | 18.93 | -18.93 | 0.29 | 318.35 | 83.45 | 54.8 | 64.68 | 11.17 | -0.98 | 9.76 | -74.8 | 980 | 8765 | 108.62 | 0.88 | -152.41 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 1185342.14 | 224283.22 | 20230204-162602_4e869081-fd05-470c-99e3-3f4cf39634b1 | 54.855
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 511.43 | 7.8 | [51.11, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [48.61, 9.44] | 0 | 1831.3 | 91.11 | 51.95 | 39.16 | 7.25 | 0 | 85 | 20.4 | 8.1 | 18.54 | -18.54 | 0.28 | 327.32 | 86.15 | 57.64 | 66.51 | 9.65 | -0.94 | 9.69 | -77.59 | 980 | 8765 | 108.62 | 0.88 | -150.72 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1029279.74 | 190517.28 | 20230204-163228_d4aac477-4f9f-441e-9337-757c6a96df4a | 47.8746
0 | 8.1 | 516.31 | 7.8 | [49.94, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [47.44, 9.44] | 0 | 1833.48 | 89.94 | 51.95 | 37.99 | 7.24 | 0 | 76 | 21.8 | 8.1 | 18.74 | -18.74 | 0.28 | 330.44 | 86.91 | 57.92 | 67.15 | 9.52 | -0.94 | 9.68 | -76.13 | 980 | 8765 | 108.62 | 0.88 | -151.2 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1016340.7 | 190517.28 | 20230204-163228_f4d9136d-7c5f-4115-bed5-81e02ade9b44 | 47.136
0 | 8.1 | 2913.32 | 7.8 | [17.92, 47.64] | [29.0, 4.31] | [0.0, 0.0] | [4.42, 9.44] | 0 | 2089.61 | 46.92 | 51.95 | -5.03 | 7.18 | 0 | 89 | 18.9 | 8.1 | 17.56 | -17.56 | 1.39 | 1864.52 | 478.85 | 275.03 | 380 | 4.97 | 0.4 | 6.99 | -85.58 | 980 | 8765 | 108.62 | 0.88 | 275.56 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 416274.55 | 190517.28 | 20230204-163228_44f0f0bd-fd82-44c2-9d63-55e7a60fb289 | 12.8857
0 | 8.1 | 608.05 | 7.8 | [50.86, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [33.36, 9.44] | 0 | 2020.42 | 75.86 | 51.95 | 23.91 | 7.35 | 0 | 71 | 22.2 | 8.1 | 18.46 | -18.46 | 0.3 | 389.15 | 102.44 | 68.2 | 79.13 | 8.03 | -0.8 | 9.4 | -78.17 | 980 | 8765 | 108.62 | 0.88 | -155.39 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 690128.84 | 190517.28 | 20230204-163228_392e2257-671b-4dee-85c8-35d8b238f46b | 28.5166
0 | 8.1 | 1383.29 | 7.8 | [22.8, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [10.3, 8.5] | 0 | 2050.08 | 52.8 | 51 | 1.8 | 7.2 | 0 | 90 | 18.8 | 8.1 | 17.59 | -17.59 | 0.67 | 885.31 | 228.35 | 134.94 | 180.34 | 6.21 | -0.19 | 8.19 | -85.37 | 980 | 8765 | 108.62 | 0.88 | -333.98 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 492552.27 | 224283.22 | 20230204-163228_1d886f71-5eac-4070-a368-052da601ac6c | 15.3122
0 | 8.1 | 694.65 | 7.8 | [39.93, 38.87] | [29.0, 11.36] | [0.0, 0.0] | [26.43, 7.73] | 0 | 2000.63 | 68.93 | 50.23 | 18.7 | 7.28 | 0 | 85 | 20.1 | 8.1 | 18.25 | -18.25 | 0.35 | 444.58 | 116.19 | 74.39 | 90.45 | 8.92 | -0.72 | 9.23 | -79.82 | 980 | 8765 | 108.62 | 0.88 | -166.4 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 659169.41 | 251909.9 | 20230204-163228_5af75082-cda2-4678-a54d-ff0127ab1b83 | 23.2454
0 | 8.1 | 497.07 | 7.8 | [46.04, 42.81] | [49.0, 8.19] | [0.0, 0.0] | [52.54, 8.5] | 0 | 1740.65 | 95.04 | 51 | 44.04 | 7.18 | 0 | 77 | 22.2 | 8.1 | 19.25 | -19.25 | 0.29 | 318.13 | 83.46 | 55 | 64.63 | 11.18 | -0.98 | 9.75 | -72.64 | 980 | 8765 | 108.62 | 0.88 | -152.04 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 1175108.01 | 224283.22 | 20230204-163228_e4972e1b-d56c-4881-86fe-46218ff5ef74 | 54.2708
0 | 8.1 | 942.01 | 7.8 | [34.32, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [16.82, 9.44] | 0 | 2083.31 | 59.32 | 51.95 | 7.37 | 7.29 | 0 | 81 | 21.4 | 8.1 | 19 | -19 | 0.45 | 602.89 | 156.95 | 98 | 122.73 | 6.28 | -0.48 | 8.76 | -74.3 | 980 | 8765 | 108.62 | 0.88 | -198.28 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 507609.87 | 190517.28 | 20230204-163228_961034e0-fa5a-4d68-a862-515841e08b48 | 18.0989
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 2431.01 | 7.8 | [18.89, 32.79] | [29.0, 16.25] | [0.0, 0.0] | [5.39, 6.54] | 0 | 2084.98 | 47.89 | 49.04 | -1.15 | 7.18 | 0 | 95 | 18.9 | 8.1 | 18.29 | -18.29 | 1.17 | 1555.85 | 399.93 | 231.04 | 317.07 | 7.32 | 0.26 | 7.28 | -79.46 | 980 | 8765 | 108.62 | 0.88 | 654.5 | 103.87 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 426956.19 | 294412.49 | 20230204-163228_b4cd858d-cbe2-462f-b0a3-1e74a4df1bca | 7.5653
0 | 8.1 | 730.08 | 7.8 | [36.9, 38.87] | [30.0, 11.36] | [0.0, 0.0] | [24.4, 7.73] | 0 | 1996.38 | 66.9 | 50.23 | 16.67 | 7.26 | 0 | 90 | 19 | 8.1 | 17.78 | -17.78 | 0.37 | 467.25 | 121.86 | 77.07 | 95.08 | 8.66 | -0.68 | 9.16 | -83.64 | 980 | 8765 | 108.62 | 0.88 | -171.25 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 648145.78 | 251909.9 | 20230204-163228_6d69ac3d-5298-427f-9cd3-2d5b0d1ca158 | 22.6162
0 | 8.1 | 646.4 | 7.8 | [42.36, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [29.85, 8.5] | 0 | 1978.5 | 72.36 | 51 | 21.36 | 7.28 | 0 | 94 | 18.6 | 8.1 | 17.87 | -17.87 | 0.33 | 413.7 | 108.3 | 70.02 | 84.15 | 8.51 | -0.77 | 9.34 | -82.88 | 980 | 8765 | 108.62 | 0.88 | -161.33 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 708390.11 | 224283.22 | 20230204-163228_6f48bf9a-3fb6-48df-8f49-6f2209e4b3af | 27.6317
0 | 8.1 | 876.07 | 7.8 | [30.11, 38.87] | [31.0, 11.36] | [0.0, 0.0] | [18.6, 7.73] | 0 | 2005.26 | 61.11 | 50.23 | 10.88 | 7.22 | 0 | 87 | 19.7 | 8.1 | 18.1 | -18.1 | 0.44 | 560.68 | 145.48 | 89.28 | 114.14 | 7.91 | -0.55 | 8.9 | -80.96 | 980 | 8765 | 108.62 | 0.88 | -192.9 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 595606.98 | 251909.9 | 20230204-163228_05325a78-0675-4039-8882-cffcc3b78bc6 | 19.6174
0 | 8.1 | 936.64 | 7.8 | [40.46, 38.87] | [19.0, 11.36] | [0.0, 0.0] | [16.95, 7.73] | 0 | 2154.15 | 59.46 | 50.23 | 9.23 | 7.36 | 0 | 75 | 21.9 | 8.1 | 18.7 | -18.7 | 0.43 | 599.45 | 156.75 | 100.26 | 122.01 | 7.69 | -0.47 | 8.74 | -76.38 | 980 | 8765 | 108.62 | 0.88 | -192.19 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 440739.39 | 251909.9 | 20230204-163228_c57d0b80-8e56-42bc-8721-1c36d262d6ef | 10.7779
0 | 8.1 | 500.36 | 7.8 | [46.07, 42.81] | [48.0, 8.19] | [0.0, 0.0] | [51.56, 8.5] | 0 | 1751.2 | 94.07 | 51 | 43.07 | 7.18 | 0 | 75 | 22.2 | 8.1 | 18.99 | -18.99 | 0.29 | 320.23 | 84.01 | 55.36 | 65.06 | 11.07 | -0.97 | 9.74 | -74.39 | 980 | 8765 | 108.62 | 0.88 | -152.08 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 1153005.37 | 224283.22 | 20230204-163228_b5a51695-f7fc-43bc-b477-c4f3e78d5541 | 53.0093
0 | 8.1 | 524.8 | 7.8 | [47.05, 47.64] | [41.0, 4.31] | [0.0, 0.0] | [45.55, 9.44] | 0 | 1827.34 | 88.05 | 51.95 | 36.1 | 7.23 | 0 | 77 | 21.8 | 8.1 | 18.87 | -18.87 | 0.29 | 335.87 | 88.18 | 58.2 | 68.26 | 9.32 | -0.93 | 9.66 | -75.21 | 980 | 8765 | 108.62 | 0.88 | -152.39 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1006911.78 | 190517.28 | 20230204-163228_34a68c8f-5108-4dd4-9e08-83271423bc71 | 46.5979
0 | 8.1 | 680.42 | 7.8 | [49.85, 47.64] | [20.0, 4.31] | [0.0, 0.0] | [27.35, 9.44] | 0 | 2096.51 | 69.85 | 51.95 | 17.9 | 7.38 | 0 | 72 | 22.2 | 8.1 | 18.59 | -18.59 | 0.32 | 435.47 | 114.57 | 75.91 | 88.57 | 7.4 | -0.71 | 9.22 | -77.19 | 980 | 8765 | 108.62 | 0.88 | -160.82 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 566838.51 | 190517.28 | 20230204-163228_cc6641b5-feb8-4e28-8b26-7e4531ffb807 | 21.4795
0 | 8.1 | 576.31 | 7.8 | [41.54, 47.64] | [38.0, 4.31] | [0.0, 0.0] | [37.04, 9.44] | 0 | 1874.84 | 79.54 | 51.95 | 27.59 | 7.22 | 0 | 87 | 20 | 8.1 | 18.4 | -18.4 | 0.31 | 368.84 | 96.49 | 62.34 | 75 | 8.42 | -0.86 | 9.53 | -78.66 | 980 | 8765 | 108.62 | 0.88 | -156.83 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 878779.17 | 190517.28 | 20230204-163228_8e3e2b9d-9802-44f5-9363-e1daa40f923d | 39.2844
0 | 8.1 | 591.7 | 7.8 | [46.65, 47.64] | [31.0, 4.31] | [0.0, 0.0] | [35.15, 9.44] | 0 | 1952.05 | 77.65 | 51.95 | 25.7 | 7.29 | 0 | 69 | 22.6 | 8.1 | 18.57 | -18.57 | 0.3 | 378.69 | 99.41 | 65.33 | 77 | 8.22 | -0.83 | 9.47 | -77.38 | 980 | 8765 | 108.62 | 0.88 | -155.87 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 778194.61 | 190517.28 | 20230204-163228_567ee266-6182-44d0-ba87-68d0b96308dd | 33.5432
0 | 8.1 | 866.2 | 7.8 | [31.41, 30.41] | [30.0, 18.17] | [0.0, 0.0] | [18.91, 6.07] | 0 | 2015.89 | 61.41 | 48.58 | 12.83 | 7.24 | 0 | 94 | 18.7 | 8.1 | 17.97 | -17.97 | 0.43 | 554.37 | 143.99 | 88.87 | 112.85 | 10.11 | -0.55 | 8.91 | -82.04 | 980 | 8765 | 108.62 | 0.88 | -190.46 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 587537.99 | 311109.93 | 20230204-163228_ab778cfe-e213-44de-aaf0-af4f25431fe8 | 15.7779
0 | 8.1 | 566.93 | 7.8 | [50.81, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [38.31, 8.5] | 0 | 1953.42 | 80.81 | 51 | 29.81 | 7.31 | 0 | 70 | 22.5 | 8.1 | 18.61 | -18.61 | 0.29 | 362.83 | 95.5 | 63.66 | 73.76 | 9.51 | -0.86 | 9.52 | -77.08 | 980 | 8765 | 108.62 | 0.88 | -153.04 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 801705.95 | 224283.22 | 20230204-163228_7d42abf7-549f-4481-94b0-d74d24357abe | 32.9579
0 | 8.1 | 1699.24 | 7.8 | [20.58, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [8.07, 9.44] | 0 | 2059.73 | 50.58 | 51.95 | -1.37 | 7.18 | 0 | 88 | 19.3 | 8.1 | 17.84 | -17.84 | 0.82 | 1087.51 | 279.96 | 163.4 | 221.58 | 5.35 | -0.03 | 7.86 | -83.2 | 980 | 8765 | 108.62 | 0.88 | -620.65 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 467997.69 | 190517.28 | 20230204-163228_084d391c-0574-44fc-983f-3db91734c9a8 | 15.8379
0 | 8.1 | 517.67 | 7.8 | [50.62, 47.64] | [39.0, 4.31] | [0.0, 0.0] | [47.12, 9.44] | 0 | 1843.68 | 89.62 | 51.95 | 37.67 | 7.25 | 0 | 82 | 20.7 | 8.1 | 18.45 | -18.45 | 0.28 | 331.31 | 87.18 | 58.22 | 67.32 | 9.49 | -0.93 | 9.67 | -78.23 | 980 | 8765 | 108.62 | 0.88 | -151.03 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1001464.81 | 190517.28 | 20230204-163228_232f0df2-d2fd-4d6a-9561-76ac96f8409f | 46.287
0 | 8.1 | 624.88 | 7.8 | [45.22, 42.81] | [29.0, 8.19] | [0.0, 0.0] | [31.72, 8.5] | 0 | 1983.38 | 74.22 | 51 | 23.22 | 7.3 | 0 | 91 | 19.3 | 8.1 | 18.2 | -18.2 | 0.32 | 399.92 | 104.89 | 68.53 | 81.33 | 8.73 | -0.79 | 9.38 | -80.18 | 980 | 8765 | 108.62 | 0.88 | -158.59 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 717548.49 | 224283.22 | 20230204-163228_ef90db46-46d1-4da8-8236-3e2a514ce119 | 28.1544
0 | 8.1 | 1636.76 | 7.8 | [30.94, 47.64] | [20.0, 4.31] | [0.0, 0.0] | [8.43, 9.44] | 0 | 2185.75 | 50.94 | 51.95 | -1.01 | 7.31 | 0 | 82 | 21.2 | 8.1 | 18.94 | -18.94 | 0.75 | 1047.53 | 272.03 | 166.96 | 213.36 | 5.39 | -0.03 | 7.86 | -74.75 | 980 | 8765 | 108.62 | 0.88 | -432.48 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 358089.24 | 190517.28 | 20230204-163228_211f9cc0-c6b3-48d3-91a3-1ed4d03c7f63 | 9.5646
0 | 8.1 | 754.19 | 7.8 | [40.69, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [23.19, 9.44] | 0 | 2057.23 | 65.69 | 51.95 | 13.74 | 7.31 | 0 | 89 | 20.2 | 8.1 | 18.84 | -18.84 | 0.37 | 482.68 | 126.23 | 80.96 | 98.21 | 6.96 | -0.65 | 9.09 | -75.4 | 980 | 8765 | 108.62 | 0.88 | -171.5 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 577917.17 | 190517.28 | 20230204-163852_8ad59907-34b7-4839-9946-9cfea0696c68 | 22.1119
0 | 8.1 | 28744.97 | 7.8 | [18.92, 47.64] | [24.0, 4.31] | [0.0, 0.0] | [0.42, 9.44] | 0 | 2178.09 | 42.92 | 51.95 | -9.03 | 7.22 | 0 | 91 | 19.9 | 8.1 | 18.79 | -18.79 | 13.2 | 18396.78 | 4729.4 | 2727.04 | 3750.12 | 4.54 | 2.3 | 3.21 | -75.74 | 980 | 8765 | 108.62 | 0.88 | 8.91 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 315145.3 | 190517.28 | 20230204-163852_a0238ab2-eec5-4580-a9b7-395b2a5cf700 | 7.1135
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 619.76 | 7.8 | [49.7, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [32.2, 9.44] | 0 | 2024.36 | 74.7 | 51.95 | 22.75 | 7.34 | 0 | 67 | 22.7 | 8.1 | 18.39 | -18.39 | 0.31 | 396.65 | 104.34 | 69.19 | 80.66 | 7.91 | -0.79 | 9.38 | -78.7 | 980 | 8765 | 108.62 | 0.88 | -156.55 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 677295.97 | 190517.28 | 20230204-163852_1304ddfc-af5f-4c90-81db-1d63ad22f719 | 27.7842
0 | 8.1 | 2456.08 | 7.8 | [47.83, 47.83] | [0.0, 0.0] | [0.0, 0.0] | [5.33, 5.33] | 0 | 2465.36 | 47.83 | 47.83 | 0 | 7.56 | 0 | 70 | 21.7 | 8.1 | 17.86 | -17.86 | 1 | 1571.89 | 413.17 | 270.29 | 320.06 | 8.98 | 0.34 | 7.12 | -82.96 | 980 | 8765 | 108.62 | 0.88 | -28867.43 | 127.48 | 60 | 9 | 9 | 0.36 | 588 | 591.2 | 96034.87 | 96034.87 | 20230204-163852_ad8b0826-c7db-4aa8-9ca0-ed0a3d544bb5 | 0
0 | 8.1 | 2344.4 | 7.8 | [48.11, 48.11] | [0.0, 0.0] | [0.0, 0.0] | [5.61, 5.61] | 0 | 2463.09 | 48.11 | 48.11 | 0 | 7.56 | 0 | 71 | 21.7 | 8.1 | 17.99 | -17.99 | 0.95 | 1500.42 | 394.45 | 258.31 | 305.5 | 8.58 | 0.3 | 7.19 | -81.86 | 980 | 8765 | 108.62 | 0.88 | -2254.19 | 121.08 | 60 | 9 | 9 | 0.37 | 588 | 591.37 | 99139.3 | 99139.3 | 20230204-163852_84c1a374-b60c-4693-b453-c83eb51da72b | 0
0 | 8.1 | 2881.21 | 7.8 | [46.98, 46.98] | [0.0, 0.0] | [0.0, 0.0] | [4.47, 4.47] | 0 | 2472.29 | 46.98 | 46.98 | 0 | 7.56 | 0 | 69 | 22 | 8.1 | 18.01 | -18.01 | 1.17 | 1843.98 | 484.43 | 315.92 | 375.49 | 10.5 | 0.47 | 6.86 | -81.73 | 980 | 8765 | 108.62 | 0.88 | 656.72 | 151.8 | 60 | 9 | 9 | 0.3 | 588 | 590.68 | 86612.73 | 86612.73 | 20230204-163852_1fd1339f-62ab-4dcb-8781-3a8d1dbcf50a | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1926.42 | 7.8 | [49.49, 49.49] | [0.0, 0.0] | [0.0, 0.0] | [6.99, 6.99] | 0 | 2452.14 | 49.49 | 49.49 | 0 | 7.56 | 0 | 71 | 21.6 | 8.1 | 17.9 | -17.9 | 0.79 | 1232.91 | 324.41 | 213.49 | 251.01 | 7.08 | 0.14 | 7.51 | -82.64 | 980 | 8765 | 108.62 | 0.88 | -506.66 | 97.14 | 60 | 9 | 9 | 0.47 | 588 | 592.19 | 114399.45 | 114399.45 | 20230204-163852_57893447-e073-4651-a9f3-1eb7a23f4001 | 0
0 | 8.1 | 659.37 | 7.8 | [46.34, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [28.84, 9.44] | 0 | 2036.1 | 71.34 | 51.95 | 19.39 | 7.33 | 0 | 69 | 22.4 | 8.1 | 18.38 | -18.38 | 0.32 | 422 | 110.77 | 72.59 | 85.83 | 7.55 | -0.74 | 9.29 | -78.77 | 980 | 8765 | 108.62 | 0.88 | -160.65 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 640273.88 | 190517.28 | 20230204-163852_872877e1-d342-4fbe-9992-136e0723f9d9 | 25.671
0 | 8.1 | 1725.56 | 7.8 | [50.43, 50.43] | [0.0, 0.0] | [0.0, 0.0] | [7.93, 7.93] | 0 | 2444.83 | 50.43 | 50.43 | 0 | 7.57 | 0 | 68 | 22 | 8.1 | 17.88 | -17.88 | 0.71 | 1104.36 | 290.75 | 191.97 | 224.82 | 6.36 | 0.05 | 7.69 | -82.83 | 980 | 8765 | 108.62 | 0.88 | -369.22 | 85.62 | 60 | 9 | 9 | 0.53 | 588 | 592.76 | 124784.83 | 124784.83 | 20230204-163852_27fbb9ed-067a-4ce1-a42b-25e407e39ad5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 609.09 | 7.8 | [49.75, 47.64] | [26.0, 4.31] | [0.0, 0.0] | [33.25, 9.44] | 0 | 2010.23 | 75.75 | 51.95 | 23.8 | 7.33 | 0 | 70 | 22.5 | 8.1 | 18.61 | -18.61 | 0.3 | 389.81 | 102.54 | 68.03 | 79.26 | 8.02 | -0.8 | 9.41 | -77.08 | 980 | 8765 | 108.62 | 0.88 | -155.84 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 700341.89 | 190517.28 | 20230204-163852_614230fe-fc29-4f43-b2ec-be9f90d430a5 | 29.0996
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 2175.59 | 7.8 | [48.6, 48.6] | [0.0, 0.0] | [0.0, 0.0] | [6.1, 6.1] | 0 | 2459.21 | 48.6 | 48.6 | 0 | 7.56 | 0 | 71 | 21.8 | 8.1 | 18.09 | -18.09 | 0.88 | 1392.38 | 366.16 | 240.2 | 283.49 | 7.97 | 0.24 | 7.32 | -81.1 | 980 | 8765 | 108.62 | 0.88 | -941.87 | 111.42 | 60 | 9 | 9 | 0.41 | 588 | 591.66 | 104510.42 | 104510.42 | 20230204-163852_6b79eb15-c747-46dd-b538-1f564e6d7aab | 0
0 | 8.1 | 1106.41 | 7.8 | [32.1, 47.64] | [24.0, 4.31] | [0.0, 0.0] | [13.6, 9.44] | 0 | 2109.76 | 56.1 | 51.95 | 4.15 | 7.28 | 0 | 68 | 22.1 | 8.1 | 17.97 | -17.97 | 0.52 | 708.11 | 184.04 | 113.73 | 144.18 | 5.94 | -0.35 | 8.5 | -82.05 | 980 | 8765 | 108.62 | 0.88 | -228.41 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 460638.41 | 190517.28 | 20230204-163852_b4201c25-4eac-4d7f-b1da-c17070788bbc | 15.4179
0 | 8.1 | 621.14 | 7.8 | [49.57, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [32.06, 9.44] | 0 | 2024.81 | 74.57 | 51.95 | 22.62 | 7.34 | 0 | 70 | 22.5 | 8.1 | 18.61 | -18.61 | 0.31 | 397.53 | 104.56 | 69.31 | 80.84 | 7.9 | -0.79 | 9.37 | -77.08 | 980 | 8765 | 108.62 | 0.88 | -156.69 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 675850.6 | 190517.28 | 20230204-163852_21dfcd71-d61f-4eac-9b8e-58136c6f9045 | 27.7017
0 | 8.1 | 1707.66 | 7.8 | [50.53, 50.53] | [0.0, 0.0] | [0.0, 0.0] | [8.03, 8.03] | 0 | 2444.09 | 50.53 | 50.53 | 0 | 7.57 | 0 | 80 | 21.1 | 8.1 | 18.59 | -18.59 | 0.7 | 1092.9 | 287.75 | 190.06 | 222.49 | 6.29 | 0.05 | 7.71 | -77.25 | 980 | 8765 | 108.62 | 0.88 | -360.51 | 84.59 | 60 | 9 | 9 | 0.54 | 588 | 592.82 | 125848.31 | 125848.31 | 20230204-163852_683d379c-0c81-4f9b-8c14-b13444fa99b3 | 0
0 | 8.1 | 1172.62 | 7.8 | [30.13, 47.64] | [25.0, 4.31] | [0.0, 0.0] | [12.63, 9.44] | 0 | 2101.96 | 55.13 | 51.95 | 3.18 | 7.27 | 0 | 74 | 21.9 | 8.1 | 18.57 | -18.57 | 0.56 | 750.48 | 194.75 | 119.28 | 152.83 | 5.84 | -0.31 | 8.42 | -77.33 | 980 | 8765 | 108.62 | 0.88 | -245.68 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 461321.05 | 190517.28 | 20230204-163852_93192c66-2e60-4b7d-9c3f-3cbb3931a92c | 15.4568
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 2575.58 | 7.8 | [47.56, 47.56] | [0.0, 0.0] | [0.0, 0.0] | [5.06, 5.06] | 0 | 2467.55 | 47.56 | 47.56 | 0 | 7.56 | 0 | 73 | 21.5 | 8.1 | 18.07 | -18.07 | 1.04 | 1648.37 | 433.2 | 283.11 | 335.64 | 9.41 | 0.38 | 7.04 | -81.27 | 980 | 8765 | 108.62 | 0.88 | 2481 | 134.31 | 60 | 9 | 9 | 0.34 | 588 | 591.03 | 93040.81 | 93040.81 | 20230204-163852_93e25903-9081-437c-909a-bb62432b2205 | 0
0 | 8.1 | 3204.8 | 7.8 | [46.49, 46.49] | [0.0, 0.0] | [0.0, 0.0] | [3.99, 3.99] | 0 | 2476.28 | 46.49 | 46.49 | 0 | 7.56 | 0 | 68 | 22 | 8.1 | 17.88 | -17.88 | 1.29 | 2051.07 | 538.67 | 350.66 | 417.67 | 11.66 | 0.56 | 6.69 | -82.83 | 980 | 8765 | 108.62 | 0.88 | 369.22 | 170.3 | 60 | 9 | 9 | 0.27 | 588 | 590.39 | 81247.35 | 81247.35 | 20230204-163852_9ab28186-2862-4a22-956c-3c4522b45ac2 | 0
0 | 8.1 | 1864.14 | 7.8 | [49.76, 49.76] | [0.0, 0.0] | [0.0, 0.0] | [7.26, 7.26] | 0 | 2450.05 | 49.76 | 49.76 | 0 | 7.57 | 0 | 79 | 21.5 | 8.1 | 18.84 | -18.84 | 0.76 | 1193.05 | 313.97 | 206.81 | 242.89 | 6.86 | 0.12 | 7.57 | -75.41 | 980 | 8765 | 108.62 | 0.88 | -454.23 | 93.57 | 60 | 9 | 9 | 0.48 | 588 | 592.35 | 117344.72 | 117344.72 | 20230204-163852_be190a79-6a95-47c8-b05f-e74f9439b3bc | 0
0 | 8.1 | 2874.63 | 7.8 | [46.99, 46.99] | [0.0, 0.0] | [0.0, 0.0] | [4.49, 4.49] | 0 | 2472.2 | 46.99 | 46.99 | 0 | 7.56 | 0 | 73 | 21.8 | 8.1 | 18.35 | -18.35 | 1.16 | 1839.76 | 483.32 | 315.21 | 374.63 | 10.48 | 0.47 | 6.86 | -79.03 | 980 | 8765 | 108.62 | 0.88 | 667.29 | 151.42 | 60 | 9 | 9 | 0.3 | 588 | 590.69 | 86735.58 | 86735.58 | 20230204-163852_71345143-f3b8-45fa-a817-ff2dc27eaef5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1398.71 | 7.8 | [52.66, 52.66] | [0.0, 0.0] | [0.0, 0.0] | [10.16, 10.16] | 0 | 2427.97 | 52.66 | 52.66 | 0 | 7.57 | 0 | 64 | 19.2 | 8.1 | 14.79 | -14.79 | 0.58 | 895.18 | 235.99 | 157.01 | 182.21 | 5.18 | -0.11 | 8.03 | -121.05 | 980 | 8765 | 108.62 | 0.88 | -256.24 | 66.83 | 60 | 9 | 9 | 0.68 | 588 | 594.1 | 149401.44 | 149401.44 | 20230204-164514_80d71a9e-77a5-407d-8711-3581c0b54066 | 0
0 | 8.1 | 2045.75 | 7.8 | [49.03, 49.03] | [0.0, 0.0] | [0.0, 0.0] | [6.53, 6.53] | 0 | 2455.75 | 49.03 | 49.03 | 0 | 7.56 | 0 | 74 | 18.8 | 8.1 | 15.65 | -15.65 | 0.83 | 1309.28 | 344.4 | 226.28 | 266.57 | 7.51 | 0.19 | 7.42 | -107.29 | 980 | 8765 | 108.62 | 0.88 | -650.62 | 103.98 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 109323.36 | 109323.36 | 20230204-164514_14fce8ee-f0ec-4a1f-8f9b-92d3d9e56dde | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1454.97 | 7.8 | [52.19, 52.19] | [0.0, 0.0] | [0.0, 0.0] | [9.69, 9.69] | 0 | 2431.47 | 52.19 | 52.19 | 0 | 7.57 | 0 | 67 | 19.6 | 8.1 | 15.53 | -15.53 | 0.6 | 931.18 | 245.42 | 163.02 | 189.54 | 5.38 | -0.08 | 7.96 | -108.97 | 980 | 8765 | 108.62 | 0.88 | -270.48 | 70.07 | 60 | 9 | 9 | 0.65 | 588 | 593.82 | 144215.87 | 144215.87 | 20230204-164514_ecad33ea-fca9-4346-a073-2836924fb682 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 2400.42 | 7.8 | [47.97, 47.97] | [0.0, 0.0] | [0.0, 0.0] | [5.46, 5.46] | 0 | 2464.26 | 47.97 | 47.97 | 0 | 7.56 | 0 | 81 | 18.8 | 8.1 | 16.5 | -16.5 | 0.97 | 1536.27 | 403.84 | 264.32 | 312.81 | 8.78 | 0.32 | 7.16 | -96.45 | 980 | 8765 | 108.62 | 0.88 | -4193.3 | 124.29 | 60 | 9 | 9 | 0.36 | 588 | 591.28 | 97542.05 | 97542.05 | 20230204-164514_79317119-6a13-417d-baf4-283685540ca9 | 0
0 | 8.1 | 1307.61 | 7.8 | [53.53, 53.53] | [0.0, 0.0] | [0.0, 0.0] | [11.03, 11.03] | 0 | 2421.58 | 53.53 | 53.53 | 0 | 7.57 | 0 | 64 | 19.6 | 8.1 | 15.16 | -15.16 | 0.54 | 836.87 | 220.74 | 147.29 | 170.33 | 4.85 | -0.17 | 8.14 | -114.79 | 980 | 8765 | 108.62 | 0.88 | -236.13 | 61.58 | 60 | 9 | 9 | 0.74 | 588 | 594.62 | 158967.29 | 158967.29 | 20230204-164514_6231f9f2-fdd2-4368-a36a-7fc610eaaee7 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1775.22 | 7.8 | [50.18, 50.18] | [0.0, 0.0] | [0.0, 0.0] | [7.68, 7.68] | 0 | 2446.8 | 50.18 | 50.18 | 0 | 7.57 | 0 | 70 | 22.2 | 8.1 | 18.33 | -18.33 | 0.73 | 1136.14 | 299.07 | 197.29 | 231.3 | 6.54 | 0.08 | 7.64 | -79.18 | 980 | 8765 | 108.62 | 0.88 | -395.76 | 88.47 | 60 | 9 | 9 | 0.51 | 588 | 592.61 | 121964.17 | 121964.17 | 20230204-164514_839e933d-fbbc-4c9f-a003-fc9a71d216bb | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1269.46 | 7.8 | [53.94, 53.94] | [0.0, 0.0] | [0.0, 0.0] | [11.44, 11.44] | 0 | 2418.6 | 53.94 | 53.94 | 0 | 7.57 | 0 | 73 | 18.7 | 8.1 | 15.43 | -15.43 | 0.52 | 812.46 | 214.35 | 143.22 | 165.36 | 4.72 | -0.19 | 8.18 | -110.45 | 980 | 8765 | 108.62 | 0.88 | -228.62 | 59.37 | 60 | 9 | 9 | 0.76 | 588 | 594.86 | 163480.78 | 163480.78 | 20230204-164514_ecc3eece-6e90-44e7-8b84-d5beb58184ad | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 4322.06 | 7.8 | [45.4, 45.4] | [0.0, 0.0] | [0.0, 0.0] | [2.9, 2.9] | 0 | 2485.34 | 45.4 | 45.4 | 0 | 7.56 | 0 | 62 | 19.6 | 8.1 | 14.9 | -14.9 | 1.74 | 2766.12 | 725.95 | 470.66 | 563.33 | 15.65 | 0.8 | 6.2 | -119.05 | 980 | 8765 | 108.62 | 0.88 | 146.98 | 234.16 | 60 | 9 | 9 | 0.19 | 588 | 589.74 | 69244.18 | 69244.18 | 20230204-164514_a5249d55-0fac-457b-9e58-f6215028f2e2 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1733.39 | 7.8 | [50.39, 50.39] | [0.0, 0.0] | [0.0, 0.0] | [7.89, 7.89] | 0 | 2445.15 | 50.39 | 50.39 | 0 | 7.57 | 0 | 68 | 22.1 | 8.1 | 17.97 | -17.97 | 0.71 | 1109.37 | 292.06 | 192.81 | 225.84 | 6.39 | 0.06 | 7.68 | -82.05 | 980 | 8765 | 108.62 | 0.88 | -373.17 | 86.07 | 60 | 9 | 9 | 0.53 | 588 | 592.73 | 124327.32 | 124327.32 | 20230204-164514_4fe29a84-02e9-4731-8a3f-8b8a9cd627a9 | 0
0 | 8.1 | 2537.49 | 7.8 | [17.64, 21.1] | [30.0, 25.65] | [0.0, 0.0] | [5.14, 4.25] | 0 | 2073.03 | 47.64 | 46.75 | 0.89 | 7.17 | 0 | 52 | 21 | 8.1 | 14.83 | -14.83 | 1.22 | 1624 | 416.96 | 239.17 | 330.97 | 11.21 | 0.29 | 7.22 | -120.29 | 980 | 8765 | 108.62 | 0.88 | 484.83 | 159.79 | 60 | 9 | 9 | 0.28 | 588 | 590.55 | 435601.34 | 376229.97 | 20230204-165137_c295c30f-170f-446e-93cd-7100bdc267ab | 3.3888
0 | 8.1 | 581.63 | 7.8 | [48.86, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [36.36, 9.44] | 0 | 1958.95 | 78.86 | 51.95 | 26.91 | 7.3 | 0 | 67 | 19.4 | 8.1 | 15.35 | -15.35 | 0.3 | 372.24 | 97.86 | 64.8 | 75.68 | 8.35 | -0.84 | 9.48 | -111.75 | 980 | 8765 | 108.62 | 0.88 | -154.5 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 780185.39 | 190517.28 | 20230204-165137_80245d9c-ca9b-4b15-90d8-d1451956c24a | 33.6569
0 | 8.1 | 1428.08 | 7.8 | [22.41, 35.58] | [30.0, 14.01] | [0.0, 0.0] | [9.91, 7.08] | 0 | 2051.73 | 52.41 | 49.59 | 2.82 | 7.19 | 0 | 58 | 20.8 | 8.1 | 15.46 | -15.46 | 0.7 | 913.97 | 235.66 | 138.97 | 186.19 | 7.4 | -0.17 | 8.14 | -109.98 | 980 | 8765 | 108.62 | 0.88 | -357.36 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 488272.88 | 274932.14 | 20230204-165137_9621d0bf-4c6a-46cc-8757-cb5eb4044f98 | 12.177
0 | 8.1 | 1690.1 | 7.8 | [50.63, 50.63] | [0.0, 0.0] | [0.0, 0.0] | [8.13, 8.13] | 0 | 2443.34 | 50.63 | 50.63 | 0 | 7.57 | 0 | 63 | 19.9 | 8.1 | 15.3 | -15.3 | 0.69 | 1081.66 | 284.81 | 188.18 | 220.2 | 6.23 | 0.04 | 7.72 | -112.45 | 980 | 8765 | 108.62 | 0.88 | -352.35 | 83.58 | 60 | 9 | 9 | 0.54 | 588 | 592.88 | 126917.3 | 126917.3 | 20230204-165137_1c14ce1a-dfc5-4646-8807-d96978ce9869 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 858.62 | 7.8 | [31.64, 32.79] | [30.0, 16.25] | [0.0, 0.0] | [19.14, 6.54] | 0 | 2015.01 | 61.64 | 49.04 | 12.6 | 7.24 | 0 | 63 | 20.4 | 8.1 | 15.76 | -15.76 | 0.43 | 549.52 | 142.76 | 88.21 | 111.86 | 9.43 | -0.56 | 8.92 | -105.78 | 980 | 8765 | 108.62 | 0.88 | -189.28 | 103.87 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 590163.17 | 294412.49 | 20230204-165137_d633fee3-c775-453b-99c0-6054e444eeec | 16.8807
0 | 8.1 | 1985.4 | 7.8 | [25.26, 32.79] | [24.0, 16.25] | [0.0, 0.0] | [6.76, 6.54] | 0 | 2143.29 | 49.26 | 49.04 | 0.22 | 7.25 | 0 | 74 | 19 | 8.1 | 15.84 | -15.84 | 0.93 | 1270.66 | 328.46 | 196.23 | 258.87 | 7.53 | 0.11 | 7.58 | -104.68 | 980 | 8765 | 108.62 | 0.88 | -1474.52 | 103.87 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 385115.84 | 294412.49 | 20230204-165137_ad972651-7591-4bd0-a4fa-91be4000cca2 | 5.1771
0 | 8.1 | 752.04 | 7.8 | [35.8, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [23.29, 8.5] | 0 | 2000.16 | 65.8 | 51 | 14.8 | 7.25 | 0 | 65 | 19.5 | 8.1 | 15.19 | -15.19 | 0.38 | 481.31 | 125.42 | 78.95 | 97.94 | 7.74 | -0.66 | 9.12 | -114.23 | 980 | 8765 | 108.62 | 0.88 | -174.08 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 635981.35 | 224283.22 | 20230204-165137_95364b8d-c523-4e87-b884-1cae28969ae8 | 23.4988
0 | 8.1 | 750.97 | 7.8 | [35.85, 35.58] | [30.0, 14.01] | [0.0, 0.0] | [23.35, 7.08] | 0 | 1999.98 | 65.85 | 49.59 | 16.26 | 7.25 | 0 | 62 | 20.3 | 8.1 | 15.54 | -15.54 | 0.38 | 480.62 | 125.25 | 78.86 | 97.8 | 9.3 | -0.66 | 9.12 | -108.9 | 980 | 8765 | 108.62 | 0.88 | -173.94 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 636550.45 | 274932.14 | 20230204-165137_8604d278-3aad-43ea-bda4-86f580182269 | 20.6403
0 | 8.1 | 619.73 | 7.8 | [44.7, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [32.2, 9.44] | 0 | 1971.24 | 74.7 | 51.95 | 22.75 | 7.29 | 0 | 61 | 20.4 | 8.1 | 15.5 | -15.5 | 0.31 | 396.63 | 103.99 | 67.84 | 80.66 | 7.91 | -0.8 | 9.4 | -109.47 | 980 | 8765 | 108.62 | 0.88 | -158.43 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 734271.51 | 190517.28 | 20230204-165137_61379513-1a10-45da-a506-17b1d58992b0 | 31.0362
0 | 8.1 | 655.18 | 7.8 | [41.66, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [29.16, 8.5] | 0 | 1980.69 | 71.66 | 51 | 20.66 | 7.28 | 0 | 60 | 20.4 | 8.1 | 15.37 | -15.37 | 0.33 | 419.31 | 109.72 | 70.75 | 85.29 | 8.43 | -0.76 | 9.32 | -111.43 | 980 | 8765 | 108.62 | 0.88 | -162.32 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 700737.52 | 224283.22 | 20230204-165137_1ad3bebf-ae09-44ab-ae51-d0dd3b712525 | 27.1949
0 | 8.1 | 853.2 | 7.8 | [34.82, 35.58] | [27.0, 14.01] | [0.0, 0.0] | [19.32, 7.08] | 0 | 2049.42 | 61.82 | 49.59 | 12.23 | 7.27 | 0 | 63 | 20.3 | 8.1 | 15.67 | -15.67 | 0.42 | 546.05 | 142.2 | 89.05 | 111.14 | 8.73 | -0.56 | 8.92 | -107.05 | 980 | 8765 | 108.62 | 0.88 | -186.1 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 557918.83 | 274932.14 | 20230204-165137_ed6c7eee-d2e2-4d7a-93ee-5165566a2390 | 16.1522
0 | 8.1 | 576.7 | 7.8 | [49.49, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [36.99, 9.44] | 0 | 1957.15 | 79.49 | 51.95 | 27.54 | 7.31 | 0 | 61 | 20.6 | 8.1 | 15.68 | -15.68 | 0.29 | 369.09 | 97.07 | 64.41 | 75.04 | 8.42 | -0.85 | 9.5 | -106.87 | 980 | 8765 | 108.62 | 0.88 | -154 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 787112.81 | 190517.28 | 20230204-165137_b3c632c6-212c-4083-9a0a-b35a3a3f3f9d | 34.0523
0 | 8.1 | 2438.68 | 7.8 | [47.87, 47.87] | [0.0, 0.0] | [0.0, 0.0] | [5.37, 5.37] | 0 | 2465.02 | 47.87 | 47.87 | 0 | 7.56 | 0 | 67 | 19.4 | 8.1 | 15.35 | -15.35 | 0.99 | 1560.75 | 410.25 | 268.42 | 317.79 | 8.92 | 0.33 | 7.13 | -111.75 | 980 | 8765 | 108.62 | 0.88 | -10165.78 | 126.48 | 60 | 9 | 9 | 0.36 | 588 | 591.22 | 96497.89 | 96497.89 | 20230204-165137_cff838f3-6e5d-4516-81e5-19207da7ac79 | 0
0 | 8.1 | 600.92 | 7.8 | [46.61, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [34.11, 9.44] | 0 | 1965.5 | 76.61 | 51.95 | 24.66 | 7.3 | 0 | 68 | 19.5 | 8.1 | 15.57 | -15.57 | 0.31 | 384.59 | 100.96 | 66.32 | 78.2 | 8.11 | -0.82 | 9.44 | -108.5 | 980 | 8765 | 108.62 | 0.88 | -156.46 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 755390.31 | 190517.28 | 20230204-165137_348859cd-0c7c-4d38-8271-ee07aa4de376 | 32.2416
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 618.91 | 7.8 | [44.78, 42.81] | [30.0, 8.19] | [0.0, 0.0] | [32.28, 8.5] | 0 | 1971.01 | 74.78 | 51 | 23.78 | 7.29 | 0 | 65 | 19.8 | 8.1 | 15.47 | -15.47 | 0.31 | 396.11 | 103.86 | 67.77 | 80.55 | 8.8 | -0.8 | 9.4 | -109.97 | 980 | 8765 | 108.62 | 0.88 | -158.35 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 735134.1 | 224283.22 | 20230204-165137_1f05bf9e-1871-439a-bc77-80884210212d | 29.1582
0 | 8.1 | 750.86 | 7.8 | [35.85, 35.58] | [30.0, 14.01] | [0.0, 0.0] | [23.35, 7.08] | 0 | 1999.97 | 65.85 | 49.59 | 16.26 | 7.25 | 0 | 66 | 19.6 | 8.1 | 15.41 | -15.41 | 0.38 | 480.55 | 125.23 | 78.85 | 97.79 | 9.3 | -0.66 | 9.12 | -110.84 | 980 | 8765 | 108.62 | 0.88 | -173.92 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 636609.84 | 274932.14 | 20230204-165137_cbcf051a-c141-4f24-afb4-f24ce0d0a08b | 20.6437
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 750.57 | 7.8 | [35.87, 35.58] | [30.0, 14.01] | [0.0, 0.0] | [23.36, 7.08] | 0 | 1999.92 | 65.87 | 49.59 | 16.28 | 7.25 | 0 | 64 | 19.8 | 8.1 | 15.34 | -15.34 | 0.38 | 480.37 | 125.19 | 78.83 | 97.75 | 9.3 | -0.66 | 9.12 | -111.89 | 980 | 8765 | 108.62 | 0.88 | -173.88 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 636759.62 | 274932.14 | 20230204-165137_51dfde6a-b18d-4e17-b0ae-86defcc16b18 | 20.6523
0 | 8.1 | 817.62 | 7.8 | [33.05, 32.79] | [30.0, 16.25] | [0.0, 0.0] | [20.54, 6.54] | 0 | 2009.89 | 63.05 | 49.04 | 14.01 | 7.24 | 0 | 57 | 20.3 | 8.1 | 14.89 | -14.89 | 0.41 | 523.28 | 136.08 | 84.63 | 106.51 | 9.64 | -0.6 | 9 | -119.32 | 980 | 8765 | 108.62 | 0.88 | -183.12 | 103.87 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 605638.33 | 294412.49 | 20230204-165137_64528c0b-c434-498c-ba96-3fe28a466488 | 17.764
0 | 8.1 | 2349.36 | 7.8 | [19.1, 20.07] | [29.0, 26.48] | [0.0, 0.0] | [5.6, 4.05] | 0 | 2084 | 48.1 | 46.55 | 1.55 | 7.18 | 0 | 55 | 20.9 | 8.1 | 15.15 | -15.15 | 1.13 | 1503.59 | 386.57 | 223.59 | 306.41 | 11.88 | 0.23 | 7.34 | -114.84 | 980 | 8765 | 108.62 | 0.88 | 853.08 | 167.78 | 60 | 9 | 9 | 0.27 | 588 | 590.43 | 429246.6 | 383465.53 | 20230204-165137_e48cf637-8546-40cf-8686-cc24dc108b34 | 2.6131
0 | 8.1 | 750.73 | 7.8 | [35.86, 35.58] | [30.0, 14.01] | [0.0, 0.0] | [23.36, 7.08] | 0 | 1999.94 | 65.86 | 49.59 | 16.27 | 7.25 | 0 | 63 | 19.8 | 8.1 | 15.21 | -15.21 | 0.38 | 480.47 | 125.21 | 78.84 | 97.77 | 9.3 | -0.66 | 9.12 | -113.89 | 980 | 8765 | 108.62 | 0.88 | -173.9 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 636678.27 | 274932.14 | 20230204-165137_6103b2d8-87eb-43a1-861e-f31ce45dd85e | 20.6476
0 | 8.1 | 699.9 | 7.8 | [38.6, 38.87] | [30.0, 11.36] | [0.0, 0.0] | [26.1, 7.73] | 0 | 1990.63 | 68.6 | 50.23 | 18.37 | 7.27 | 0 | 60 | 20.1 | 8.1 | 15.1 | -15.1 | 0.35 | 447.93 | 116.96 | 74.5 | 91.13 | 8.88 | -0.71 | 9.22 | -115.72 | 980 | 8765 | 108.62 | 0.88 | -167.53 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 666990.39 | 251909.9 | 20230204-165137_ce5974f5-1ab8-43a8-9cf0-58cb35b8613a | 23.6918
0 | 8.1 | 1407.97 | 7.8 | [42.58, 42.81] | [10.0, 8.19] | [0.0, 0.0] | [10.08, 8.5] | 0 | 2302.71 | 52.58 | 51 | 1.58 | 7.45 | 0 | 72 | 18.8 | 8.1 | 15.41 | -15.41 | 0.61 | 901.1 | 236.01 | 151.82 | 183.46 | 6.19 | -0.13 | 8.06 | -110.87 | 980 | 8765 | 108.62 | 0.88 | -279.56 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 262393.13 | 224283.22 | 20230204-165137_701f1cfc-208c-4cf1-bce0-1049c6a0ea13 | 2.1752
0 | 8.1 | 2385.07 | 7.8 | [26.0, 26.53] | [22.0, 21.28] | [0.0, 0.0] | [5.5, 5.31] | 0 | 2176.04 | 48 | 47.81 | 0.19 | 7.27 | 0 | 64 | 20.5 | 8.1 | 15.98 | -15.98 | 1.1 | 1526.45 | 394.83 | 236.64 | 311 | 9.04 | 0.26 | 7.27 | -102.82 | 980 | 8765 | 108.62 | 0.88 | 1130.79 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 348507.41 | 338243.28 | 20230204-165802_af3c21dd-bf35-48d1-8638-df86aa5dfe04 | 0.58585
0 | 8.1 | 3648.88 | 7.8 | [23.97, 42.81] | [22.0, 8.19] | [0.0, 0.0] | [3.47, 8.5] | 0 | 2187.48 | 45.97 | 51 | -5.03 | 7.27 | 0 | 66 | 20.1 | 8.1 | 15.87 | -15.87 | 1.67 | 2335.29 | 603.03 | 357.55 | 475.87 | 5.41 | 0.61 | 6.58 | -104.28 | 980 | 8765 | 108.62 | 0.88 | 162.59 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 326073.38 | 224283.22 | 20230204-165802_882cfc9b-5391-4bb1-9670-8bf01bddd76b | 5.8099
0 | 8.1 | 2061.51 | 7.8 | [25.98, 30.41] | [23.0, 18.17] | [0.0, 0.0] | [6.48, 6.07] | 0 | 2157.73 | 48.98 | 48.58 | 0.4 | 7.27 | 0 | 61 | 20.5 | 8.1 | 15.59 | -15.59 | 0.96 | 1319.37 | 341.26 | 204.57 | 268.79 | 8.07 | 0.14 | 7.51 | -108.15 | 980 | 8765 | 108.62 | 0.88 | -2435.83 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 370626.72 | 311109.93 | 20230204-165802_1a0064e4-d9c3-491e-a096-ef05933c299f | 3.3971
0 | 8.1 | 3599.12 | 7.8 | [24.02, 24.02] | [22.0, 22.0] | [0.0, 0.0] | [3.52, 3.52] | 0 | 2187.19 | 46.02 | 46.02 | 0 | 7.27 | 0 | 70 | 20.3 | 8.1 | 16.56 | -16.56 | 1.65 | 2303.44 | 594.83 | 352.78 | 469.38 | 13.07 | 0.6 | 6.6 | -95.75 | 980 | 8765 | 108.62 | 0.88 | 168.27 | 192.84 | 60 | 9 | 9 | 0.23 | 588 | 590.11 | 326638.39 | 326638.39 | 20230204-165802_2d2cd15a-700d-48b2-af08-4b6af76811f8 | 0
0 | 8.1 | 2046.08 | 7.8 | [24.03, 32.79] | [25.0, 16.25] | [0.0, 0.0] | [6.53, 6.54] | 0 | 2131.5 | 49.03 | 49.04 | -0.01 | 7.24 | 0 | 73 | 20.1 | 8.1 | 16.75 | -16.75 | 0.96 | 1309.49 | 338.14 | 200.78 | 266.8 | 7.5 | 0.13 | 7.53 | -93.64 | 980 | 8765 | 108.62 | 0.88 | -2710.66 | 103.87 | 60 | 9 | 9 | 0.44 | 588 | 591.92 | 394010.23 | 294412.49 | 20230204-165802_632d1e26-5042-464a-8260-eedaac13669f | 5.6848
0 | 8.1 | 1577.23 | 7.8 | [26.31, 30.41] | [25.0, 18.17] | [0.0, 0.0] | [8.81, 6.07] | 0 | 2120.11 | 51.31 | 48.58 | 2.73 | 7.25 | 0 | 61 | 20.4 | 8.1 | 15.5 | -15.5 | 0.74 | 1009.43 | 261.15 | 156.94 | 205.62 | 8.45 | -0.08 | 7.95 | -109.47 | 980 | 8765 | 108.62 | 0.88 | -424.21 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 419159.51 | 311109.93 | 20230204-165802_4afa75e7-47bc-470d-8b86-0bc9a5050d57 | 6.1672
0 | 8.1 | 1005.42 | 7.8 | [17.91, 35.58] | [40.0, 14.01] | [0.0, 0.0] | [15.41, 7.08] | 0 | 1908.72 | 57.91 | 49.59 | 8.32 | 7.1 | 0 | 79 | 19.4 | 8.1 | 16.83 | -16.83 | 0.53 | 643.47 | 165.23 | 95.32 | 131.06 | 8.18 | -0.47 | 8.74 | -92.78 | 980 | 8765 | 108.62 | 0.88 | -229.53 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 662837.94 | 274932.14 | 20230204-165802_20f46fb5-c188-4943-95dc-6439ebb32ff6 | 22.1407
0 | 8.1 | 1221.83 | 7.8 | [14.5, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [11.99, 9.44] | 0 | 1919.09 | 54.5 | 51.95 | 2.55 | 7.08 | 0 | 71 | 21 | 8.1 | 17.34 | -17.34 | 0.64 | 781.97 | 200.15 | 113.04 | 159.32 | 5.77 | -0.32 | 8.44 | -87.66 | 980 | 8765 | 108.62 | 0.88 | -298.97 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 625135.81 | 190517.28 | 20230204-165802_1e69a806-01af-404d-8d27-3dcb8095113f | 24.807
0 | 8.1 | 3061.47 | 7.8 | [24.69, 28.34] | [22.0, 19.83] | [0.0, 0.0] | [4.19, 5.67] | 0 | 2183.39 | 46.69 | 48.17 | -1.48 | 7.27 | 0 | 67 | 20.1 | 8.1 | 15.99 | -15.99 | 1.4 | 1959.34 | 506.26 | 301.33 | 399.24 | 8.24 | 0.47 | 6.87 | -102.61 | 980 | 8765 | 108.62 | 0.88 | 270.1 | 119.85 | 60 | 9 | 9 | 0.38 | 588 | 591.4 | 334008.53 | 325581.05 | 20230204-165802_cb700177-30e7-4a4a-a460-a92cdad547b6 | 0.48102
0 | 8.1 | 3596 | 7.8 | [24.03, 47.64] | [22.0, 4.31] | [0.0, 0.0] | [3.52, 9.44] | 0 | 2187.17 | 46.03 | 51.95 | -5.92 | 7.27 | 0 | 78 | 19.1 | 8.1 | 16.42 | -16.42 | 1.64 | 2301.44 | 594.31 | 352.49 | 468.97 | 4.87 | 0.6 | 6.61 | -97.34 | 980 | 8765 | 108.62 | 0.88 | 168.64 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 326674.38 | 190517.28 | 20230204-165802_f84c5deb-0886-43dd-a481-fa2d80c75aca | 7.7715
0 | 8.1 | 2839.16 | 7.8 | [24.05, 26.53] | [23.0, 21.28] | [0.0, 0.0] | [4.55, 5.31] | 0 | 2168.18 | 47.05 | 47.81 | -0.76 | 7.26 | 0 | 74 | 19.7 | 8.1 | 16.5 | -16.5 | 1.31 | 1817.06 | 469.23 | 278.44 | 370.25 | 8.86 | 0.4 | 6.99 | -96.45 | 980 | 8765 | 108.62 | 0.88 | 351.01 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 349331.77 | 338243.28 | 20230204-165802_68e7c892-cc79-4328-8501-4e2634f2ca75 | 0.6329
0 | 8.1 | 751.05 | 7.8 | [35.84, 35.58] | [30.0, 14.01] | [0.0, 0.0] | [23.34, 7.08] | 0 | 2000 | 65.84 | 49.59 | 16.25 | 7.25 | 0 | 58 | 20.4 | 8.1 | 15.11 | -15.11 | 0.38 | 480.67 | 125.26 | 78.87 | 97.81 | 9.3 | -0.66 | 9.12 | -115.58 | 980 | 8765 | 108.62 | 0.88 | -173.95 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 636506.52 | 274932.14 | 20230204-165802_3d66bad6-2018-4905-9424-37488e30796c | 20.6378
0 | 8.1 | 1015.47 | 7.8 | [17.71, 18.27] | [40.0, 27.93] | [0.0, 0.0] | [15.21, 3.7] | 0 | 1909.32 | 57.71 | 46.2 | 11.51 | 7.1 | 0 | 81 | 19.8 | 8.1 | 17.46 | -17.46 | 0.53 | 649.9 | 166.85 | 96.14 | 132.37 | 15.61 | -0.46 | 8.73 | -86.53 | 980 | 8765 | 108.62 | 0.88 | -232.03 | 183.76 | 60 | 9 | 9 | 0.25 | 588 | 590.22 | 660608.78 | 396049.11 | 20230204-165802_feb252c6-3db4-4791-9927-619e2f709f0e | 15.1004
0 | 8.1 | 1082.58 | 7.8 | [16.49, 47.64] | [40.0, 4.31] | [0.0, 0.0] | [13.99, 9.44] | 0 | 1912.97 | 56.49 | 51.95 | 4.54 | 7.09 | 0 | 80 | 20 | 8.1 | 17.53 | -17.53 | 0.57 | 692.85 | 177.67 | 101.62 | 141.14 | 5.98 | -0.42 | 8.63 | -85.9 | 980 | 8765 | 108.62 | 0.88 | -250.24 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 647120.95 | 190517.28 | 20230204-165802_70d42718-9c30-4d4f-ad14-5027e8a36bf3 | 26.0619
0 | 8.1 | 3669.94 | 7.8 | [23.95, 35.58] | [22.0, 14.01] | [0.0, 0.0] | [3.45, 7.08] | 0 | 2187.61 | 45.95 | 49.59 | -3.64 | 7.27 | 0 | 77 | 19.6 | 8.1 | 16.78 | -16.78 | 1.68 | 2348.76 | 606.5 | 359.56 | 478.62 | 6.49 | 0.61 | 6.57 | -93.37 | 980 | 8765 | 108.62 | 0.88 | 160.31 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 325839.27 | 274932.14 | 20230204-165802_4f0cadb0-e4dd-469a-98ec-db4abdf80a2a | 2.9057
0 | 8.1 | 2913.05 | 7.8 | [23.92, 30.41] | [23.0, 18.17] | [0.0, 0.0] | [4.42, 6.07] | 0 | 2168.87 | 46.92 | 48.58 | -1.66 | 7.26 | 0 | 68 | 20.2 | 8.1 | 16.21 | -16.21 | 1.34 | 1864.35 | 481.39 | 285.46 | 379.89 | 7.73 | 0.42 | 6.95 | -99.84 | 980 | 8765 | 108.62 | 0.88 | 316.58 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 347951.4 | 311109.93 | 20230204-165802_046f84fc-1da3-4660-84d7-121831a90fdd | 2.1028
0 | 8.1 | 1801 | 7.8 | [18.05, 26.53] | [32.0, 21.28] | [0.0, 0.0] | [7.55, 5.31] | 0 | 2036.34 | 50.05 | 47.81 | 2.24 | 7.16 | 0 | 80 | 19.2 | 8.1 | 16.76 | -16.76 | 0.88 | 1152.64 | 296.05 | 170.38 | 234.87 | 9.42 | 0.01 | 7.78 | -93.52 | 980 | 8765 | 108.62 | 0.88 | -939.92 | 127.83 | 60 | 9 | 9 | 0.35 | 588 | 591.19 | 484986.46 | 338243.28 | 20230204-165802_48dbed83-c165-48f4-b25c-bc3300aa41a1 | 8.3758
0 | 8.1 | 1245.92 | 7.8 | [24.21, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [11.71, 9.44] | 0 | 2044.16 | 54.21 | 51.95 | 2.26 | 7.2 | 0 | 87 | 18.6 | 8.1 | 17.03 | -17.03 | 0.61 | 797.39 | 205.92 | 122.62 | 162.41 | 5.74 | -0.28 | 8.35 | -90.72 | 980 | 8765 | 108.62 | 0.88 | -278.17 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 508078.97 | 190517.28 | 20230204-165802_2c91f3ca-5286-4a2e-ba04-95f0b8de2859 | 18.1257
0 | 8.1 | 3631.49 | 7.8 | [23.99, 23.99] | [22.0, 22.0] | [0.0, 0.0] | [3.49, 3.49] | 0 | 2187.38 | 45.99 | 45.99 | 0 | 7.27 | 0 | 64 | 20.7 | 8.1 | 16.16 | -16.16 | 1.66 | 2324.15 | 600.16 | 355.88 | 473.61 | 13.18 | 0.61 | 6.59 | -100.49 | 980 | 8765 | 108.62 | 0.88 | 164.53 | 194.69 | 60 | 9 | 9 | 0.23 | 588 | 590.09 | 326268.97 | 326268.97 | 20230204-165802_0f7d7f89-c0d1-4098-b821-85ce886c8d82 | 0
0 | 8.1 | 3687.8 | 7.8 | [23.93, 23.93] | [22.0, 22.0] | [0.0, 0.0] | [3.43, 3.43] | 0 | 2187.71 | 45.93 | 45.93 | 0 | 7.26 | 0 | 64 | 20.1 | 8.1 | 15.61 | -15.61 | 1.69 | 2360.19 | 609.44 | 361.27 | 480.95 | 13.39 | 0.62 | 6.56 | -107.82 | 980 | 8765 | 108.62 | 0.88 | 158.42 | 197.91 | 60 | 9 | 9 | 0.23 | 588 | 590.06 | 325642.91 | 325642.91 | 20230204-165802_f7152b24-dade-4b2f-a908-ae9ed2bf1916 | 0
0 | 8.1 | 3669.79 | 7.8 | [23.95, 23.95] | [22.0, 22.0] | [0.0, 0.0] | [3.45, 3.45] | 0 | 2187.61 | 45.95 | 45.95 | 0 | 7.27 | 0 | 63 | 20.6 | 8.1 | 15.94 | -15.94 | 1.68 | 2348.66 | 606.47 | 359.55 | 478.6 | 13.32 | 0.61 | 6.57 | -103.32 | 980 | 8765 | 108.62 | 0.88 | 160.32 | 196.88 | 60 | 9 | 9 | 0.23 | 588 | 590.07 | 325840.93 | 325840.93 | 20230204-165802_cce58037-06c7-4a8f-ac9b-6477d5d91f1a | 0
0 | 8.1 | 1814.73 | 7.8 | [25.99, 42.81] | [24.0, 8.19] | [0.0, 0.0] | [7.48, 8.5] | 0 | 2139.54 | 49.99 | 51 | -1.01 | 7.26 | 0 | 62 | 20.5 | 8.1 | 15.72 | -15.72 | 0.85 | 1161.43 | 300.4 | 180.16 | 236.6 | 5.88 | 0.04 | 7.72 | -106.31 | 980 | 8765 | 108.62 | 0.88 | -715.52 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 393159.16 | 224283.22 | 20230204-165802_59065f76-cfd4-413d-a65a-cbdf29b6e001 | 9.639
0 | 8.1 | 1261.43 | 7.8 | [24.03, 47.64] | [30.0, 4.31] | [0.0, 0.0] | [11.53, 9.44] | 0 | 2044.9 | 54.03 | 51.95 | 2.08 | 7.2 | 0 | 83 | 18.9 | 8.1 | 16.84 | -16.84 | 0.62 | 807.32 | 208.45 | 124.01 | 164.44 | 5.72 | -0.27 | 8.33 | -92.71 | 980 | 8765 | 108.62 | 0.88 | -283.52 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 506114.61 | 190517.28 | 20230204-165802_f7f43ea9-5675-4faa-a1dd-42022485d25e | 18.0135
0 | 8.1 | 3685.56 | 7.8 | [23.93, 23.93] | [22.0, 22.0] | [0.0, 0.0] | [3.43, 3.43] | 0 | 2187.7 | 45.93 | 45.93 | 0 | 7.27 | 0 | 69 | 20.1 | 8.1 | 16.25 | -16.25 | 1.68 | 2358.76 | 609.07 | 361.06 | 480.66 | 13.38 | 0.62 | 6.57 | -99.42 | 980 | 8765 | 108.62 | 0.88 | 158.65 | 197.78 | 60 | 9 | 9 | 0.23 | 588 | 590.06 | 325667.42 | 325667.42 | 20230204-165802_e376ac16-adb0-42f1-b114-5a1e16710594 | 0
0 | 8.1 | 3608.89 | 7.8 | [24.01, 42.81] | [22.0, 8.19] | [0.0, 0.0] | [3.51, 8.5] | 0 | 2187.25 | 46.01 | 51 | -4.99 | 7.27 | 0 | 77 | 19.7 | 8.1 | 16.87 | -16.87 | 1.65 | 2309.69 | 596.44 | 353.72 | 470.66 | 5.41 | 0.6 | 6.6 | -92.36 | 980 | 8765 | 108.62 | 0.88 | 167.12 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 326526.14 | 224283.22 | 20230204-165802_d136b641-334d-4e33-8270-2e0107193261 | 5.8358
0 | 8.1 | 2854.44 | 7.8 | [24.02, 47.64] | [23.0, 4.31] | [0.0, 0.0] | [4.52, 9.44] | 0 | 2168.33 | 47.02 | 51.95 | -4.93 | 7.26 | 0 | 76 | 19.7 | 8.1 | 16.75 | -16.75 | 1.32 | 1826.84 | 471.75 | 279.89 | 372.24 | 4.98 | 0.41 | 6.99 | -93.68 | 980 | 8765 | 108.62 | 0.88 | 343.29 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 349040.04 | 190517.28 | 20230204-165802_a9d867fd-059a-49c4-b4c6-f5974bd1e860 | 9.0481
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 1230.66 | 7.8 | [14.39, 35.58] | [40.0, 14.01] | [0.0, 0.0] | [11.89, 7.08] | 0 | 1919.42 | 54.39 | 49.59 | 4.8 | 7.08 | 0 | 83 | 19.7 | 8.1 | 17.61 | -17.61 | 0.64 | 787.62 | 201.57 | 113.77 | 160.47 | 7.68 | -0.32 | 8.43 | -85.16 | 980 | 8765 | 108.62 | 0.88 | -302.71 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 623952.58 | 274932.14 | 20230204-170424_9a50a1da-46a2-4735-a07c-50b260a7aa24 | 19.9213
0 | 8.1 | 460.58 | 7.8 | [26.8, 38.87] | [84.0, 11.36] | [0.0, 0.0] | [68.3, 7.73] | 0 | 1426.6 | 110.8 | 50.23 | 60.57 | 6.94 | 0 | 79 | 20.9 | 8.1 | 18.27 | -18.27 | 0.32 | 294.77 | 76.22 | 46.9 | 59.85 | 14.34 | -1.08 | 9.96 | -79.67 | 980 | 8765 | 108.62 | 0.88 | -160.41 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 1747684.07 | 251909.9 | 20230204-170424_a11df79a-fc8a-4c36-a17b-adaccff252b7 | 85.3752
0 | 8.1 | 1547.4 | 7.8 | [14.51, 47.64] | [37.0, 4.31] | [0.0, 0.0] | [9.01, 9.44] | 0 | 1966.73 | 51.51 | 51.95 | -0.44 | 7.1 | 0 | 84 | 19.8 | 8.1 | 17.83 | -17.83 | 0.79 | 990.33 | 253.49 | 143 | 201.81 | 5.45 | -0.13 | 8.06 | -83.23 | 980 | 8765 | 108.62 | 0.88 | -509.46 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 558027.11 | 190517.28 | 20230204-170424_b3dfb02b-0d82-43ed-89d6-16c4e5b19db6 | 20.9766
0 | 8.1 | 484.47 | 7.8 | [27.25, 35.58] | [72.0, 14.01] | [0.0, 0.0] | [56.75, 7.08] | 0 | 1527.35 | 99.25 | 49.59 | 49.66 | 6.99 | 0 | 86 | 19.6 | 8.1 | 17.88 | -17.88 | 0.32 | 310.06 | 80.22 | 49.26 | 63 | 14.01 | -1.04 | 9.88 | -82.79 | 980 | 8765 | 108.62 | 0.88 | -159.09 | 95.88 | 60 | 9 | 9 | 0.47 | 588 | 592.25 | 1483540.48 | 274932.14 | 20230204-170424_1a46f6b8-1464-4cb7-87b0-f4933f8b8ee9 | 68.9845
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 449.8 | 7.8 | [29.31, 38.87] | [90.0, 11.36] | [0.0, 0.0] | [76.81, 7.73] | 0 | 1383.31 | 119.31 | 50.23 | 69.08 | 6.93 | 0 | 83 | 19.4 | 8.1 | 17.32 | -17.32 | 0.33 | 287.87 | 74.57 | 46.52 | 58.42 | 15.44 | -1.09 | 9.99 | -87.84 | 980 | 8765 | 108.62 | 0.88 | -160.96 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 1909905.96 | 251909.9 | 20230204-170424_adf315d3-4bd4-47b8-9fb0-3bea9cab5887 | 94.6345
0 | 8.1 | 461.61 | 7.8 | [27.14, 30.41] | [83.0, 18.17] | [0.0, 0.0] | [67.64, 6.07] | 0 | 1434.67 | 110.14 | 48.58 | 61.56 | 6.94 | 0 | 70 | 21.9 | 8.1 | 18.05 | -18.05 | 0.32 | 295.43 | 76.41 | 47.08 | 59.99 | 18.14 | -1.08 | 9.96 | -81.41 | 980 | 8765 | 108.62 | 0.88 | -160.16 | 111.86 | 60 | 9 | 9 | 0.4 | 588 | 591.64 | 1729034 | 311109.93 | 20230204-170424_91035fab-2679-43fb-8bff-4fe8414e0a73 | 80.9317
0 | 8.1 | 494.15 | 7.8 | [29.94, 47.64] | [66.0, 4.31] | [0.0, 0.0] | [53.44, 9.44] | 0 | 1582.52 | 95.94 | 51.95 | 43.99 | 7.02 | 0 | 85 | 19.8 | 8.1 | 17.96 | -17.96 | 0.31 | 316.26 | 82 | 50.89 | 64.26 | 10.16 | -1.02 | 9.83 | -82.19 | 980 | 8765 | 108.62 | 0.88 | -157.94 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1378651.54 | 190517.28 | 20230204-170424_403ce1e5-02dc-4995-9410-f179587df1b6 | 67.8159
0 | 8.1 | 740.19 | 7.8 | [22.38, 42.81] | [44.0, 8.19] | [0.0, 0.0] | [23.88, 8.5] | 0 | 1840.18 | 66.38 | 51 | 15.38 | 7.1 | 0 | 85 | 19.5 | 8.1 | 17.66 | -17.66 | 0.4 | 473.72 | 122.11 | 72.38 | 96.43 | 7.81 | -0.71 | 9.22 | -84.7 | 980 | 8765 | 108.62 | 0.88 | -181.72 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 801832.6 | 224283.22 | 20230204-170424_43d46bff-d2dc-423d-8a07-53fc2cd2d5cb | 32.9651
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 455.33 | 7.8 | [28.5, 38.87] | [86.0, 11.36] | [0.0, 0.0] | [72.0, 7.73] | 0 | 1412.33 | 114.5 | 50.23 | 64.27 | 6.94 | 0 | 73 | 21.1 | 8.1 | 17.69 | -17.69 | 0.32 | 291.41 | 75.45 | 46.83 | 59.16 | 14.82 | -1.09 | 9.97 | -84.45 | 980 | 8765 | 108.62 | 0.88 | -160.31 | 87.89 | 60 | 9 | 9 | 0.52 | 588 | 592.64 | 1811268.4 | 251909.9 | 20230204-170424_fa6294b6-2f51-4461-b156-ad963cb3ab95 | 89.0045
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 589.99 | 7.8 | [27.85, 42.81] | [50.0, 8.19] | [0.0, 0.0] | [35.35, 8.5] | 0 | 1754.07 | 77.85 | 51 | 26.85 | 7.09 | 0 | 81 | 20.1 | 8.1 | 17.75 | -17.75 | 0.34 | 377.6 | 97.77 | 59.74 | 76.8 | 9.16 | -0.88 | 9.56 | -83.94 | 980 | 8765 | 108.62 | 0.88 | -163.68 | 79.9 | 60 | 9 | 9 | 0.57 | 588 | 593.1 | 996761.21 | 224283.22 | 20230204-170424_2d126446-68db-4688-afa5-5b4affe3d0bd | 44.0912
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 8.1 | 449.26 | 7.8 | [29.85, 47.64] | [90.0, 4.31] | [0.0, 0.0] | [77.35, 9.44] | 0 | 1383.76 | 119.85 | 51.95 | 67.9 | 6.93 | 0 | 86 | 19.7 | 8.1 | 17.98 | -17.98 | 0.32 | 287.52 | 74.52 | 46.6 | 58.35 | 12.69 | -1.09 | 9.99 | -81.97 | 980 | 8765 | 108.62 | 0.88 | -160.85 | 71.91 | 60 | 9 | 9 | 0.63 | 588 | 593.67 | 1915855.78 | 190517.28 | 20230204-170424_1be70015-0bd5-408c-b698-70e5caad58e7 | 98.4782

## A3
supply_temp | return_temp | ct_conductivity | ct_ph | Bore | CWRO | BoilerBD | BD | scheme | mu_conductivity | mu_flow | mu_ph | cooling_tower_level | relative_humidity | ambient_temp | delta_temp | wetBulb_temp | approach_temp | cond_coc | ct_tds | ct_ca | ct_alk | ct_chloride | flow_cycle | sat_index | sta_index | perf_index | system_vol | rec_rate | evap_loss | drift_loss | blowdown_coc | hold_time_index | dosing_residual | dosing_contact_time | dosing_density | dosing_continuous | dosing_initial | dosing_slug | currentOperatingCost | newOperatingCost | updatedDateTime
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0